

WM Group Engineers, PC


SECTION 15712

INDUCED DRAFT COOLING TOWER

Part 1. GENERAL

1.1 WORK INCLUDED

A. Furnish equipment and services necessary for a complete and safe installation in accordance with the contract documents and all applicable codes and authorities having jurisdictions for the following

1. Cooling tower (metal induced draft type).

2. Controls.

3. Ladder and handrails.

4. Water filter.

1.2 SUBMITTALS

A. Submit shop drawings indicating suggested structural steel supports including dimensions, sizes, and locations for mounting bolt holes.

B. Product data:  Catalog cuts giving rated capacities, dimensions, weights and point loadings, accessories, required clearances, electrical requirements, location and size of field connections, and schematic indicating capacity controls.

C. Certify performance, based on CTI and submit performance curve plotting leaving water temperature against wet bulb temperature.

D. Start-up report.

1.3 OPERATION AND MAINTENANCE DATA

A. Include start-up instructions, maintenance data, parts lists, controls, and accessories.

1.4 DELIVERY, STORAGE AND HANDLING

A. Factory assemble entire unit.  For shipping, disassemble into as large as practical sub-assemblies so that minimum amount of field work is required for re-assembly.

1.5 EXTRA MATERIALS

A. Provide one set of matched fan belts, three spray nozzles for each cell, one gasket for each access door, one valve seat for each make-up or control valve.

Part 2. PRODUCTS

2.1 MANUFACTURERS

A. Cooling tower.

1. Marley Cooling Tower Co.

2. Baltimore Air Coil Co., Inc.

3. BAC - Pritchard, Inc.

B. Heat Exchangers:

1. Bell & Gossett ITT.

2. Patterson-Kelley Co., Inc.

3. Taco, Inc.

C. Level Controls.

1. B/W Controller, Corp.

2. Magnetrol International, Inc.

2.2 GENERAL

A. Type:

SELECT APPLICABLE OPTION FROM THE FOLLOWING LISTINGS:

1. Crossflow - vertical discharge.

2. Crossflow - horizontal discharge.

B. Construct in accordance with:

1. Authorities having jurisdiction.

2. Wind load of 30 lb per sq ft.

C. Supports

SELECT APPLICABLE OPTION FROM THE FOLLOWING LISTINGS:

OPTION 1

1. Concrete pad:

a. Concrete under DIVISION 3.

b. See Section 15010:  GENERAL PROVISIONS - MECHANICAL.

OPTION 2

2. Structural steel:

a. Steel under DIVISION 5.

b. See Section 15010:  GENERAL PROVISIONS - MECHANICAL.

3. Vibration Eliminators:

a. See Section 15210:  VIBRATION ISOLATION AND SEISMIC CONTROL.

NOTE:
FOR TOWERS WHERE NOISE IS NOT CRITICAL OR WHERE OWNER IS WILLING TO ASSUME RISK, USE OF ONE OF THE FOLLOWING OPTIONS.  REVIEW WITH ACOUSTICAL ENGINEER.

OPTION 1

D. Noise guarantee:

1. Airborne noise emitted by cooling tower not to exceed ----- dba at a distance of ---- feet from any cooling tower surface.

2. When requested of and approved by Architect in writing, manufacturer may obtain satisfactory noise levels by oversizing equipment or providing sound attenuation.

OPTION 2

E. Noise guarantee:

INDICATE CRITICAL POINT WHERE READINGS ARE TO BE TAKEN.  SELECT APPLICABLE NC CURVE AND ADD TO VALUES FOR VARIOUS FREQUENCY BANDS (PAGE 203, 1961 ASHRAE GUIDE) AN ALLOWANCE FOR SOUND TRANSMISSION LOSS THROUGH WINDOWS (TABLE 22 ON PAGE 219,1961 ASHRAE GUIDE.)  NOTE THAT NOISE EMISSION CAN BE REDUCED BY APPROXIMATELY 13 DB BY HALF SPEED OPERATION OF FAN.  SPECIFY HALF SPEED OPERATION AT NIGHT WHERE APPLICABLE AND AVOID FAN CYCLING IF POSSIBLE

F. Performance test:

1. Factory test by manufacturer in accordance with:

INSERT TEST CRITERIA

G. Galvanized steel components:  hot dipped.

2.3 CROSSFLOW VERTICAL DISCHARGE TOWER - SCHEDULE TYPE A

A. Casing.

OPTION 1

1. Fiberglass reinforced fabric.

a. Supporting framework:  galvanized steel.

OPTION 2

2. Galvanized steel.

B. Wetted deck and eliminators:

1. Polyvinylchloride honeycomb.

2. Support in galvanized steel frames.

C. Drift Eliminators:

1. Two-pass polyvinylchloride or hot dip galvanized steel.

2. Limit drift loss to 2% of total water circulated.

D. Distribution system:

1. Gravity type distribution basin.

2. Plastic diffusion metering orifices.

3. Flanged pipe inlets for connection to condenser water piping.

4. Flow control valves.

E. Cold water basin:

1. Heavy gauge galvanized steel:

NOTE:
INSERT PROPER SHEET METAL GAUGES:  TOWER SIZE:  UP TO 200 TONS, BOTTOM NO. 12 AND SIDES NO. 12.  FROM 200 TO 350 TONS:  BOTTOM NO. 10, SIDES NO. 10.  ABOVE 350 TONS:  BOTTOM NO. 10, SIDES NO. 7.

a. Bottom:  No. ----- USSG.

b. Sides:  No. ----- USSG.

2. Built-in anticavitation sump:

a. Suction screen:  full width, stainless steel.

F. Fans:

1. Propeller type:  adjustable or fixed aluminum blades.

2. Hub:  cast iron or aluminum.

SELECT APPLICABLE OPTION FROM THE FOLLOWING LISTINGS:

3. Drive:

a. Parallel steel shaft helical gear reduction unit or

b. Multi-grooved neoprene/polyester belt drive.

NOTE:
COORDINATE WITH ELECTRICAL DEPARTMENT.

4. Fan Cylinder:

a. One-piece.

b. Welded hot dip galvanized steel assembly.

c. Full height, inlet cylinder welded to fan deck.

5. Fan Guard:  Welded, guard, rod and wire, hot dip galvanized after fabrication.

G. Motors (suitable for use in wet, corrosive environment):

NOTE:
IF TWO SPEEDS ARE REQUIRED, COORDINATE CAREFULLY WITH STARTERS.

1. In accordance with NEMA, IEEE, and ANSI C50 standards.

2. Capacity:

a. Maximum horsepower as scheduled.

b. Operate driven devices under all conditions without overload.

3. Squirrel-cage induction type, 1750 rpm, NEMA Type "B" insulation class, continuous duty.

4. Enclosure:  totally enclosed fan cooled or totally enclosed air over.

5. NEMA KVA locked rotor CODE LETTER:  "G" or better.

6. Service factor for drip-proof enclosure 1.15.

7. Bearings, except as noted:

a. Ball or roller type.

b. For horizontal and vertical application.

c. Grease lubricated:

1) With pressure type lubricating fittings similar to Alemite.

2) With Keystone pressure relief fittings.

3) Extend to accessible locations.

d. Sealed, permanently lubricated.

H. Drains

1. Valved drain from cooling tower basin sump to drain.

SELECT APPLICABLE OPTION FROM THE FOLLOWING LISTINGS:

OPTION 1

2. Overflow piping spill over nearest floor drain.

OPTION 2

3. Overflow piping spill over nearest roof drain.

NOTE:
USE WHEN APPLICABLE.

4. Drain from each cooling tower inlet and distribution bypass connections.

SELECT APPLICABLE OPTION FROM THE FOLLOWING LISTINGS:

OPTION 1

a. Drain to spill over nearest floor drain.

OPTION 2

b. Drain to spill over nearest roof drain.

NOTE:
COORDINATE WITH ELECTRICAL DEPARTMENT.

c. Solenoid valve:

1) 120 volt, 60 hertz.

2) Interlocked with respective motorized valve.

a) Close when motorized inlet valve starts to open.

b) Opens when motorized inlet valve reaches closed position.

I. Access:

1. Large doors to air plenum, safety railings, and ladder from (grade) (roof) to fan deck.

NOTE:
INCLUDE AS APPLICABLE FOR THIS JOB.

2. Provide safety cage on ladder where fan deck is 20 feet or more above tower base.

J. Similar to Marley NC Double-Flow or BAC Series 3000.

2.4 WINTERIZATION SYSTEM

A. General:

SELECT APPLICABLE OPTION FROM THE FOLLOWING LISTINGS.  BE SURE TO PROPERLY EDIT THE FOLLOWING PAGES IN ACCORDANCE WITH THE TYPE OF HEATING SPECIFIED.

1. Type:

a. Electric.

b. Steam.

c. Hot water.

2. Operative when basin contains water.

3. Distribution bypass piping to discharge into tower basin.

4. To prevent freeze-up in any part of basin or connecting piping.

5. Provide necessary piping, insulation and controls.

NOTE:
CHECK WITH COOLING TOWER MANUFACTURER FOR LOCAL AREA CONDITIONS AND FILL IN TEMPERATURES.

6. Thermal capacity:

a. Basin temperature 40oF.

b. Ambient air dry bulb temperature:  0oF.

NOTE:
FOR ELECTRIC SYSTEM.  COORDINATE WITH THE ELECTRICAL DEPARTMENT.

B. Immersion heaters:

1. Resistance wire embedded in refractory.

a. Encased in stainless steel sheath.

2. Elements:

a. Replaceable.

b. Electrical characteristics and capacity as scheduled on Drawings.

NOTE:
COORDINATE WITH ELECTRICAL DEPARTMENT.

3. Controls:

a. Thermostats:

1) 120 volt. 

2) Single pole adjustable type.

3) Stainless steel well.

b. Low water cutoff:

1) Probe type.

2) Stainless steel sheath.

3) Liquidproof outlet box.

c. Operation:  see Section 15900:  CONTROLS AND INSTRUMENTATION.

NOTE:
FOR STEAM SYSTEM SPECIFY COIL MATERIAL.

C. Steam coils in basin:

1. Pipe:  -----.

2. Inlet steam pressure:  ----- .

NOTE:
CHECK WITH COOLING TOWER MANUFACTURER FOR LOCAL AREA CONDITIONS AND FILL IN TEMPERATURE

3. Controls:

a. Thermostats:

1) 120 volt.

2) Single pole adjustable type.

3) Stainless steel well.

b. Low water cutoff:

1) Probe type.

2) Stainless steel sheath.

3) Liquidproof outlet box.

c. Steam control valve:

1) Electric or pneumatic.

2) See Section 15900:  CONTROLS AND INSTRUMENTATION.

NOTE:
FOR HOT WATER BYPASS CIRCULATION SYSTEM.  USE ONLY IF APPLICABLE TO PROJECT.

D. Hot water system:

1. Circulating pump:

a. Vertically split case type.

b. In-line circulator as specified in Section 15140:  PUMPS.

NOTE:
USE IF CONVERTER IS SPECIFIED ELSEWHERE.

2. Converter as specified in Section 15730:  HEAT EXCHANGERS.

NOTE:
USE IF CONVERTER IS NOT SPECIFIED ELSEWHERE.

3. Convertor:

a. Shell and tube.

b. Shells:  welded steel construction.

1) Flanged.

2) Dished head at end.

c. Tubes:  3/4 in. OD, copper.

d. Relief valves:  ASME

e. ASME stamped.

f. Design working pressure:  150 psi, tubes and shell.

g. Fouling factor:  .00005.

h. Water in tubes.

i. Supports:  welded pipe stand or structural base, as approved.

j. Similar to Patterson-Kelley.

NOTE:
WHEN CONNECTING PIPING REQUIRES HEAT TRACING.  COORDINATE WITH ELECTRICAL DEPARTMENT.

E. Following piping heat traced by electric resistance cable:

1. See Section 15060:  PIPE AND PIPE FITTINGS for heat trace cable.

2. (Specify piping to have trace cable.)

NOTE:
INCLUDE AS APPLICABLE FOR THIS JOB.

F. De-icing:  provide reversing fan motor and time delay relay to de-ice tower louvers during winter operation.

2.5 CONDENSER WATER MAKE-UP SYSTEM

A. Storage tank:

1. Type:  copper bearing steel, welded construction dished heads.

2. Size, capacity and arrangement, as indicated.

3. Provide tank with:

a. Saddles and structural steel or saddles and concrete floor supports.

b. Tappings, connections and piping.

c. Manhole 12 in. x 18 in.

1) With gasketed cover.

d. Protected gauge glass for full height of tank, with shutoff valves and drain cock.

NOTE:
COORDINATE WITH ELECTRICAL DEPARTMENT.

B. Level Control:

1. Pump start and stop level controller.

a. Start either or both condenser water make-up pumps when level in tank rises above high water level.

2. Displacement level controller:

a. Suitable for 120 volt, 60 hertz.

3. In accordance with ASME Code for Unfired Pressure Vessels.

4. Similar to Magnetrol Model A-103.

NOTE:
COORDINATE WITH ELECTRICAL DEPARTMENT - BE SURE OF ELECTRICAL INTERLOCK.

C. Condenser water system circulating pumps as specified in Section 15140:  PUMPS.

NOTE:
IF MAKE-UP PUMP HEAD IS HIGH, A TWO STAGE PUMP MAY BE REQUIRED

2.6 WATER LEVEL CONTROLS:

SELECT APPLICABLE OPTION FROM THE FOLLOWING LISTINGS:

FOR TOWERS USED ABOVE FREEZING TEMPERATURES AND INDOOR TOWERS

OPTION 1   FLOAT

A. Float controlled valves:

1. 1 per basin.

2. Heavy duty type.

3. Cast bronze.

4. Seamless copper or plastic ball.

OPTION 2   FLOAT

B. Float switch:

1. One or more as required to control water level per level schedule.

2. Side or top mounted.

3. Basin type or external.

4. Float or displacement type.

5. Type and configuration to suit tower.

6. Similar to Magnetrol.

NOTE:
FOR TOWER OPERATION EXTENDING BELOW FREEZING TEMPERATURE ALSO COORDINATE WITH ELECTRICAL DEPARTMENT.

OPTION 3   FLOAT

C. Electrode system:

1. 1 per basin.

2. With electrode actuating unit for:

a. Make-up water.

b. High and low water alarms.

3. Ice-free type with:

a. 350 watt immersion heater.

b. Built-in and prewired thermostat.

4. 4 electrodes:

a. Stainless steel.

b. Polyvinyl chloride insulated.

5. Top mounted at level portion of tower basin.

6. Suitable electric control relays for make-up water control.

7. Galvanized steel vented pipe cover around electrodes to prevent water waves or surges from affecting electrodes.

8. Similar to B/W Controller Corp. Type 6012-1FW.

NOTE:
INSERT HEIGHT OF WATER LEVEL IN BASIN.  INCLUDE AS APPLICABLE FOR THIS JOB OR INDICATE ON DRAWINGS.

D. Level Control Schedule:

1. Unit to open make-up water solenoid valve when basin water drops below ----- of water in basin.

2. Unit to close make-up water solenoid valve when basin water rises above ----- of water in basin.

3. Unit to start make-up water pump and open make-up water solenoid valve when basin water drops below ----- of water in basin.

4. Unit to stop make-up water pump and close make-up water solenoid valve when basin water rises above ----- of water in basin.

E. Unit to actuate high and low water alarms when water in basin rises or falls below operating levels.

F. Electrical

1. Make-up control circuits suitable for 120 volt.

2. Electrode and heater circuits:  120 volt.

3. Provide suitable transformers, if required.

2.7 ACCESSORIES

A. Hot water basin covers.

B. Inlet Screens:

1. On air inlet louvers.

2. No. 2 mesh x 0.063 galvanized wire.

NOTE:
ADD AS REQUIRED

2.8 FILTERS

Part 3. EXECUTION

3.1 INSTALLATION

A. Install tower on structural supports per manufacturer's instructions.

B. Complete piping and electrical connections per manufacturer's instructions.

3.2 REFER TO DIVISION 16, POWER, CONTROL AND ALARM WIRING SYSTEMS.

3.3 START-UP AND INSTRUCTION

NOTE:
INCLUDE THE FOLLOWING TWO CLAUSES ONLY FOR VERY LARGE JOBS.  INSERT TIME PERIOD.

A. Manufacturer's representative to inspect tower after installation is complete.

1. Submit report prior to start-up.

2. Verify installation is in accordance with specifications and manufacturer's recommendations.

B. Manufacturer's representative to supervise rigging, hoisting, and installation of cooling tower.

C. Provide manufacturer's representative for two consecutive eight hour days working per tower for start-up of cooling tower and instruction of Owner's operating personnel.

D. Make adjustments and efficiency tests when so directed by Architect.

END OF SECTION

NOTE:
REVIEW THE WORK INCLUDED ARTICLE 1.01.  FOR EACH ITEM LISTED THERE MUST BE A CORRESPONDING ARTICLE IN PART 2 AND/OR PART 3.

Amgen

Steam Turbine Drive

Chiller Conversion
15561-1
February 5, 2001

