
SECTION  13352
Owner - 13352b


DUCT TESTING, ADJUSTING, & BALANCING
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  1 May 1996

Use this Section if the Owner is to provide the testing and balancing under a separate Contract.  This is determined by the Area Office.  Edit this Section to correspond with services the Owner is requiring of the air test & balance agency and Project circumstances.

PART 1 GENERAL
 1.1
SUMMARY
A.
Air testing & balancing will be provided by Owner in accordance with special services required under Section 01100.  This specification establishes quality of performance for information of Contractor, Architect, and Owner's Representatives.

B.
Related Sections

1.
Division 15 -

a.
Complete installation and start mechanical systems, and make changes in sheaves, belts, and dampers.

b.
Repair of leaks in ductwork.

c.
Assist the Balancing Agency in the testing and balancing of mechanical system.

 1.2
SYSTEM DESCRIPTION
A.
Performance Requirements

1.
Furnish supervision, personnel, instruments, calibration equipment, and other materials and services to perform work of this Section.

2.
Test, balance, and adjust air heating, cooling, and exhaust systems as described in Contract Documents.  Perform testing and balancing in complete accordance with Associated Air Balance Council Standards for Field Measurement & Instructions, Form P1266, Volume I.  Record test data on AABC standard forms or facsimile.

3.
Smoke test low pressure steel duct systems.

4.
Noise level shall not exceed PNC 35 in Chapel or Cultural Center when all mechanical equipment is operating.

 1.3
SUBMITTALS
A.
Quality Control

1.
Submit four copies of complete test data to Architect for evaluation and approval.  Include in air balance report letter indicating smoke testing has been accomplished and report of findings regarding airtightness of each ducted system.

2.
Test & Balance Report - 

a.
Report will be complete with logs, data, and records as required herein.  Submit logs, data, and records on white bond paper bound together in report form.

b.
Report will be certified accurate and complete by Balancing Agency's certified test and balance engineer.

c.
Report will contain following general data in format selected by Balancing Agency.

1)
Project Number

2)
Project Title

3)
Project Location

4)
Project Architect and Mechanical Engineer

5)
Test and Balance Agency and Certified Engineer

6)
Contractor and mechanical sub-contractor

7)
Dates tests were performed

8)
Certification Document

9)
Report Forms similar to AABC Standard format.

d.
Report will include following -

1)
Preface suggesting abnormalities and problems encountered

2)
Instrumentation List including type, model, manufacturer, serial number, and calibration dates.

3)
System Identification reporting location of VAV boxes, zones, supply, return, and exhaust openings.

4)
Record following for each piece of air handling equipment.

a)
Manufacturer, model number, and serial number

b)
Design and manufacturer rated data

c)
Actual CFM

d)
Suction and discharge static pressure of each fan

e)
Outside-air and return-air total CFM

f)
Actual operating current, voltage, and brake horsepower of each fan motor

g)
Final RPM of each motor

h)
Fan and motor sheave manufacturer, model, size, number of grooves and center distance

i)
Belt size and quantity

j)
Static-pressure controls final operating set points

3.
Submit approved copy of report for inclusion in Division 15 Operations & Maintenance Manual.

 1.4
QUALITY ASSURANCE
A.
Qualifications  -  Work of this Section will be performed by independent Air Testing & Balance Agency specializing in testing and balancing of heating, ventilating, and cooling systems to balance, adjust, and test air moving equipment, air distribution, and exhaust systems.

 1.5
SCHEDULING
A.
Test and balance subcontract will be awarded to Agency upon confirmation of receipt of Notice To Proceed to allow Agency to schedule this work in cooperation with other Sections involved and to comply with completion date.

B.
During construction, Agency will inspect installation of pipe systems, sheet metal work, temperature controls, and other component parts of mechanical systems.  Perform inspections as follows

1.
One inspection when 60 percent of duct work is installed.

2.
One inspection when 90 percent of equipment is installed. 

C.
Schedule smoke testing before ducts being wrapped where duct wrapping is required by Contract Documents, or, if ducts are not wrapped, in sufficient time to allow for sealing of leaks before testing and balancing of mechanical system.

D.
Do not begin air testing and balancing until

1.
After completion of air cooling, heating, and exhaust systems including installation of specialties, devices, and new filters.

2.
Proper function of control system components including electrical interlocks, damper sequences, air and water reset, and fire and freeze stats has been verified.

3.
Automatic temperature controls have been calibrated and set for design operating conditions.

4.
Verification of proper thermostat calibration and setting of control components such as static pressure controllers and other devices that may need set points changed during process of balancing system.

E.
Heating, ventilating, and cooling systems and equipment shall be in full operation and continue in operation during each working day of testing and balancing.

PART 2 PRODUCTS  -  Not Used

PART 3 EXECUTION
 3.1
FIELD QUALITY CONTROL
A.
Site Tests

1.
If requested, conduct tests in presence of Architect.

2.
Instruments used by Agency will be accurately calibrated and maintained in good working order.

3.
Smoke Testing Procedure -

a.
Test each low pressure duct system.

b.
Use zinc chloride smoke candles, titanium tetrachloride ampules (sticks), or other devices approved by Architect, to generate smoke.

c.
Provide temporary portable fan as required to pressurize and circulate smoke into each duct system.

d.
Close openings in duct except for one opening at farthest end of duct runs.

e.
Circulate smoke at pressurized condition of 1/2 inch minimum water gauge static pressure.

f.
Report findings to Architect in writing.

g.
Retest systems which are found to have leaks, after proper sealing by Division 15.

4.
Air Testing & Balancing Procedure -

a.
Perform tests at high and low speeds of multi-speed systems and single speed systems.  Perform following testing and balancing functions in accordance with Associated Air Balance Council National Standards -

1)
Fan Speeds  -  Test and adjust fan RPM to achieve design CFM requirements.

2)
Current and Voltage  -  Measure and record motor current and voltage.

3)
Pitot-tube Traverse  -  Perform Pitot-tube traverse of main supply and return ducts to obtain total CFM. 

4)
Outside Air  -  Test and adjust system minimum outside air by Pitot-tube traverse.

5)
Static Pressure  -  Test and record system static pressures, including suction and discharge static pressure of each fan.

6)
Air Temperature  -  Take wet and dry bulb air temperatures on entering and leaving side of each cooling coil.  Dry bulb temperatures will be taken on entering and leaving side of each heating unit.

7)
Zone Ducts  -  Adjust zone ducts to within design CFM requirements.  At least one zone balancing damper shall be completely open.

8)
Main Ducts  -  Adjust main ducts to within design CFM requirements and traverse for total CFM quantities.

9)
Branch Ducts  -  Adjust branch ducts to within design CFM requirements.  Multi-diffuser branch ducts shall have at least one outlet or inlet volume damper completely open.

10)
Tolerances  -  Test and balance each diffuser, grille, and register to within 10 percent of design requirements.

11)
Identification  -  Identify the location and area of each grille, diffuser, register, and terminal box.  Record on air outlet data sheets.

12)
Description  -  Record size, type, and manufacturer of each diffuser, grille, and register on air outlet data sheets.

13)
Terminal Boxes  -  Set volume regulators on terminal boxes to meet design maximum and minimum CFM requirements.  Check temperature controls for proper operation and calibration.  Read out diffusers connected to terminal boxes shall be read out in heating and cooling modes and record their readings on air outlet data sheets.

14)
Drafts  -  Adjust diffusers, grilles, and registers to minimize drafts.

b.
Permanently mark all outside air, supply air, and return air damper positions after balancing has been completed.

B.
Final Inspection & Adjustments -

1.
System will be balanced and reports submitted to Architect before prefinal inspection.

2.
Agency will be represented at final inspection meeting by qualified testing personnel with balancing equipment and two copies of air balancing test report.

a.
Architect will choose and direct spot balancing of one zone.  Differences between the spot balance and test report will be justification for requiring repeat of testing and balancing for entire building.  If recheck testing demonstrates measured flow deviation of 10 percent or more from recorded information on report, report will be rejected and new inspection and report will be made and resubmitted.

b.
Agency will be prepared to spot smoke test one ducted system as directed by Architect.

c.
Rebalancing will be done in presence of Architect and subject to its approval.

d.
If re-balancing is required, submit revised air test & balance reports to Architect before Substantial Completion.

3.
Where furnace supplied to job site provides over 5 percent more air than schedule requirements, rooms supplied by that furnace shall have their supply air quantities increased by ratio of actual total air quantity supplied to minimum air quantity required by furnace schedule.


END OF SECTION

Project Number
4
13352

Project Name
Project Date
Duct Testing, Adjusting, & Balancing


