
SECTION  13353
Master - 13353a


PIPE TESTING, ADJUSTING, & BALANCING
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  4 Sep 1997

Use this optional Section if the Contractor is to include the testing and balancing of a hot water or steam heating system in his Contract.  This is determined by the Area Office.

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Testing, balancing, and adjusting of hot water heating system as described in Contract Documents.

 1.2
SUBMITTALS
A.
Quality Assurance  -  Submit four copies of complete test data for evaluation and approval.  Include neatly typed listing of items required by Contract Documents.

B.
Closeout Submittals  -  Approved copy of water test and balance report.  Include with Division 15 Operations & Maintenance Manual Data submission.

 1.3
QUALITY ASSURANCE
A.
Qualifications

1.
Procure services of an independent Testing & Balancing Agency which specializes in balancing and testing of system to balance, adjust, and test water systems and equipment.

2.
Agency shall provide proof of having successfully completed at least five projects of similar size and scope.

3.
Agency shall be approved in writing by Architect.

4.
Work by Agency shall be performed under direct supervision of qualified Heating and Ventilating Engineer employed by Agency.

5.
Neither Architect's consulting engineer nor anyone performing work on this Project under Division 15 shall be permitted to do this work.

 1.4
SEQUENCING
A.
Award test and balance subcontract to approved agency upon receipt of Notice To Proceed to allow Agency to schedule this work in cooperation with work of other Sections involved and to comply with completion date.

B.
Begin testing & balancing upon completion of cooling and heating systems including installation of all specialties and devices.

C.
Begin work of this Section after heating, ventilating, and cooling systems and equipment are in full operation and continue their operation during each working day of testing and balancing.

PART 2 PRODUCTS  -  Not Used

PART 3 EXECUTION
 3.1
FIELD QUALITY CONTROL
A.
Site Tests

1.
Instruments used by Agency shall be accurately cali​brated and maintained in good working order.

2.
Balance & Testing Agency shall provide technicians with following instruments for field use

a.
One set of pressure gauges and fittings

b.
Dry bulb thermometer

c.
Wet bulb thermometer

d.
Thermocouple unit and thermocouples

e.
Set of balancing cock adjustment wrenches

f.
Portable field flowmeter

3.
If requested, conduct tests in presence of Architect.

4.
Preparation of System  -  Phase I

a.
Open valves to full position including coil stop valves, close bypass valves, and return line balancing cocks.

b.
Remove and clean strainers. 

c.
Examine water in system to determine if it has been treated and is clean.

d.
Check pump rotation.

e.
Check expansion tanks to make sure they are not air bound and system is full of water.

f.
Check air vents at high points of water systems to make sure they are installed properly and are operating freely. Make certain air is removed from circulating system.

g.
To balance coils, set system to call for full heating.

h.
Check operation of automatic bypass valve.

i.
Check and set operating temperature of boilers to design requirements.

j.
Perform air balance before beginning water balance.

5.
Performance of Testing & Balancing  -  Phase II

a.
Set condenser water and hot water pumps to proper gpm delivery.

b.
Adjust flow of hot water through boilers and condensers.

c.
Check leaving water temperatures, return water temperatures, and pressure drop through boilers.  Reset to correct design temperatures.  Include condensers.

d.
Check water temperature at inlet side of heating coils.  Note rise or drop of temperatures from source.

e.
Balance each hot water coil.

f.
Upon completion of flow readings and coil adjustments, mark settings and record data.

6.
Performance of Testing & Balancing  -  Phase III

a.
After making adjustments to coils, recheck settings at pumps and boilers.  Readjust if required.

b.
Install pressure gauges on each coil, then read pressure drop through coil at set flow rate on call for full heating.  Set pressure drop across bypass valve to match coil full blow pressure drop.  This prevents unbalanced flow conditions when coils are on full bypass.

c.
Check and record the following items at each heating element -

1)
Inlet water and air temperatures

2)
Leaving water and air temperatures

3)
Pressure drop of each coil

4)
Pressure drop across bypass valve

5)
Pump operating suction and discharge pressures and final TDH

6)
Mechanical specifications of pumps

7)
Rated and actual running amperage of pump motor


END OF SECTION

ADVANCE \d252
B L A N K   P A G E

Project Number
3
13353

Project Name
Project Date
Pipe Testing, Adjusting, & Balancing


