
SECTION  13354
Master - 13354b


FONT WATER ADJUSTING & BALANCING
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  4 Sep 1997

Use this Section if the Owner is provide for the testing and balancing separate from the Contract with the General Contractor.  This is determined by the Area Office.

PART 1 GENERAL
 1.1
SUMMARY
A.
Font water system balancing and adjusting will be provided by Owner in accordance with special services required under Section 01100.  This specification establishes quality of performance for information on Contractor, Architect, and Owner's Representatives.

B.
Related Sections

1.
Division 15 -

a.
Complete installation and start-up of plumbing systems, including hot water heater, as required for correct balance.

b.
Assist Balancing Agency in balancing of Font water system.

 1.2
SUBMITTALS
A.
Quality Control  -  Include a copy of balancing report with each copy of font water adjusting and balancing report submitted under Section 13354 for Architect's evaluation and approval.  Include in report letter indicating balancing has been accomplished and report of hot and cold water balancing device settings.

 1.3
QUALITY ASSURANCE
A.
Qualifications  -  Work of this Section will be performed by independent Testing & Balance Agency specializing in testing and balancing of heating, ventilating, and cooling systems.

 1.4
SCHEDULING
A.
Balancing and adjusting subcontract will be awarded to Agency upon confirmation of receipt of Notice To Proceed to allow Agency to schedule this work in cooperation with other Sections involved and to comply with completion date.

B.
During construction, Agency shall inspect installation of piping systems and water heaters.

C.
Do not begin balancing and adjusting until

1.
After completion of potable hot and cold water systems including installation of water heaters, specialties, and devices.

2.
Verification of proper thermostat calibration and setting of control components and correct operation of water heater.

D.
Plumbing system and equipment shall be in full operation and continue in operation during each working day of balancing and adjusting.

PART 2 PRODUCTS  -  Not Used

PART 3 EXECUTION
 3.1
FIELD QUALITY CONTROL
A.
Site Tests

1.
If requested, conduct tests in presence of Architect.

2.
Instruments used by Agency will be accurately calibrated and maintained in good working order.

3.
Balancing & Adjusting Procedure -

a.
Open main Font water supply valve.  Set hot water balancing device first.  Set device for three gpm flow.  Set cold water balancing device so temperature gauge reads 100 deg F.  Close main supply valve.

b.
Verify settings by opening Font supply valve and checking temperature gauge reading and hot water balancing device setting.  Adjust as required.  Close Font supply valve.

B.
Final Inspection & Adjustments

1.
Balance system and submit reports to Architect before prefinal inspection.

2.
Balancing Agency will be represented at final inspection meeting by qualified testing personnel with balancing equipment and two copies of balancing and adjusting report.

3.
Agency will be prepared to verify Font water supply balance data as directed by Architect.


END OF SECTION

Project Number
1
13354

Project Name
Project Date
Font Water Adjusting & Balancing


