ELC Des Guide
SECTION  13852
Master - 13852


DETECTION & DOOR HOLDING SYSTEMS
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Electrical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  20 Oct 1997

20 Oct 97 -
Revised product specification format to comply with Section 01600.

Use this Section if the Project does not have a full alarm system as specified in Section 13851, but door holding capabilites are desired.  Door hold-open capabilities are authorized only at Chapels, Cultural Centers, Serving Areas, and Material Centers.

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnish and install detection and door holding devices as described in Contract Documents.

2.
Furnish and install raceway, conductors, boxes, and miscellaneous items necessary for complete system.

B.
Products Supplied But Not Installed Under This Section

1.
Door Plates for door hold/release devices.

C.
Related Sections

1.
Division 06 -

a.
Installation of door plates for hold/release devices.

b.
Installation of blocking for hold/release device.

2.
Division 16  -  Quality and installation requirements for electrical wiring, raceway, conduit, and boxes.

 1.2
QUALITY ASSURANCE
A.
Regulatory Requirements

1.
System shall meet approval of authority having jurisdiction (AHJ).

2.
Equipment, devices, and cable shall be UL or Factory Mutual listed.

 1.3
OWNER'S INSTRUCTIONS
A.
Instruct Owner's representative in proper operation and maintenance procedures.

PART 2 PRODUCTS
 2.1
COMPONENTS
A.
Automatic Smoke Detectors

1.
Photoelectric type with integral alarm.

2.
120 v, 60 Hz operation.

3.
Auxiliary contacts for operation of magnetic door hold/release devices.

4.
Comply with UL Standard 217.

5.
Acceptable Manufactures & Models -

a.
Simplex 2098-9667

b.
ESL 320CC

c.
Gentex 710CC

d.
Equal as approved by Architect before bidding.  See Section 01600.

B.
Door Hold/Release Devices

1.
Door release units shall be electrically operated magnetic devices which hold doors open until released by smoke detector.

2.
120 v, 60 Hz operation.

3.
Semi-flush mounting of electromagnet.

4.
Stainless steel armature.

5.
Acceptable Manufacturers & Models -

a.
Thorn/Autocall  -  FM-998-120VAC

b.
Simplex  -  2088-9559

c.
Edwards  -  1505-N5

d.
Equal as approved by Architect before bidding.  See Section 01600.

PART 3 EXECUTION
 3.1
INSTALLATION
A.
Install equipment as indicated, in accordance with equipment manufacturer's written instructions, and complying with applicable portions of NEC, NFPA and NECA's 'Standard of Installation'.

B.
Connect smoke detectors and door holders so doors are released when smoke is detected.

 3.2
FIELD QUALITY CONTROL
A.
Site Tests  -  Test operation of each detector/hold-open circuit.


END OF SECTION

Project Number
1
13852

Project Name
Project Date
Detection & Door Holding Systems


