
SECTION  14420
Supplement - 14420a


WHEELCHAIR LIFTS
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

UPDATE  -  4 Sep 1997

If the local codes do not require a wheelchair lift and a lift is shown on the Standard Plan, delete references to the lift and convert the lift space into a Storage Room.

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnish and install wheelchair lifts as described in Contract Documents.

 1.2
SUBMITTALS
A.
Product Data  -  Manufacturer's literature, operating instructions, replacement parts lists, and maintenance data including description of operation and control, and schematic wiring diagrams.

B.
Shop Drawings  -  Provide accurate shop and erection drawings and diagrams showing deviations from Drawings in ample time to make necessary adjustments in structural system of Project to fit particular equipment.  Adjustments necessary due to failure to give proper information in sufficient time to make proper adjustments shall be made without any additional cost to Owner.

 1.3
QUALITY ASSURANCE
A.
Requirements of Regulatory Agencies

1.
Obtain and pay for necessary State and Municipal permits and perform such tests as may be required for acceptance and approval by Code authority.

2.
Work and material shall conform to requirements of ANSI Safety Code for Elevators, National Electric Code, and local codes which govern requirements of installation.

 1.4
DELIVERY, STORAGE, & HANDLING
A.
Ship unit ready for installation.

 1.5
WARRANTY
A.
Submit Manufacturer's 2 year unconditional warranty on motor.

PART 2 PRODUCTS
 2.1
MANUFACTURED UNITS
A.
Wheelchair Lift

1.
Capacity  -  500 pounds

2.
Speed  -  9.6 feet per minute.

3.
Motor  -  3/4 hp, 1750 rpm, 120 volt, 60 cycle, single phase, nine amp, instant reversing.

4.
Drive  -  Ball bearing nut and screw, pulleys, and V-belts.

5.
Safety Devices -

a.
Upper, lower, and final limit switches

b.
Electro-mechanical brake

c.
Grounded electrical system

d.
24 VAC control system

e.
Ball screw safety device

f.
Nonslip surface on platform and ramp

g.
Key lock on controls

h.
Emergency stop and alarm system

i.
Equip with both mechanical and electrical contacts which prevent operation until both doors are closed.

6.
Finish  -  Flat baked enamel

Edit the list of approved manufacturers to include only those with whom you are familiar and whose products are available in the Project area.  You may add any manufacturers whose products you determine meet the specification, Project,  and local code requirements.

 2.2
ACCEPTABLE MANUFACTURERS
A.
Access Ind, Grandview, MO  (800) 925-3100

B.
National Wheel-O-Vator Co Inc, Roanoke, IL  (800) 551-9095

C.
Equal as approved by Architect before bidding.  See Section 01600.

PART 3 EXECUTION
 3.1
INSTALLATION
A.
Install lift in accordance with Manufacturer's installation manual to be included with shipment.  Do not proceed with installation without manual.

 3.2
ADJUSTING
A.
Adjust equipment to assure smooth and accurate operation.


END OF SECTION

Project Number
1
14420

Project Name
Project Date
Wheelchair Lifts


