
SECTION  15082
Master - 15082


EQUIPMENT INSULATION
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  1 May 1996

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

Paragraph 1 can be edited to state requirement for steam heating equipment insulation and the PRODUCTS and EXECUTION Parts edited accordingly.

1.
Furnish and install insulation on hot water heating system equipment as described in Contract Documents.

PART 2 PRODUCTS
 2.1
COMPONENTS
A.
Insulation

1.
1-1/2 inch thick fiberglass, 6 lb/cu ft minimum density.

2.
Approved Manufacturers -

a.
Owens-Corning type 707 

b.
Equal by -

1)
Johns-Manville

2)
Certainteed St Gobain

B.
Finish System Elements

1.
Hydraulic-setting insulating cement

2.
6 oz canvas

3.
Arabol

PART 3 EXECUTION
 3.1
INSTALLATION
A.
Install insulation on following equipment

1.
Hot water compression tanks

2.
Air separation tanks

B.
Where necessary, cut or miter insulation to fit shape and contour of equipment.  Band in place with 1/2 inch by 0.020 inch galvanized steel bands 18 inches on centers.

C.
Install suitable metal lath over fiberglass, lacing edges.

D.
Apply 1/2 inch coat of hydraulic setting insulation over lath.

E.
After cement is dry, apply one layer canvas with adhesive and apply layer of Arabol over entire surface.


END OF SECTION

Project Number
1
15082

Project Name
Project Date
Equipment Insulation


