
SECTION  15083
Master - 15083


POTABLE WATER PIPE INSULATION
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  1 Nov 1996

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

Insulate cold water piping under all conditions to prevent the possibility of freezing and/or to prevent condensation from forming on pipes.

1.
Furnish and install insulation on hot and cold water lines, fittings, valves, and accessories as described in Contract Documents.

PART 2 PRODUCTS
 2.1
INSULATION
A.
For Above Grade Piping

1.
One inch thick snap-on glass fiber or Melamine foam pipe insulation.

2.
Heavy density pipe insulation with factory vapor jacket equal to Fiberglas ASJ may be used.

3.
Approved Manufacturers -

a.
Accessible Products Inc  -  Techlite SSL

b.
Knauf

c.
Manson

d.
Owens-Corning

e.
Johns-Manville

4.
PVC Fitting, Valve, & Accessory Covers -

a.
Approved Manufacturers

1)
Accessible Products Inc  -  Techlite SSL-ASJ

2)
Knauf

3)
Zeston

B.
For Below Grade Piping

1.
1/2 inch thick

2.
Approved Manufacturers -

a.
DG Tubolit by Armstrong

b.
ImcoLock or ImcoShield by Imcoa

c.
Therma-Cel by Rubatex

3.
Joint Sealant -

a.
Armstrong 520

b.
Rubatex R-373

PART 3 EXECUTION
 3.1
APPLICATION
A.
Above Grade Piping

1.
Apply insulation to clean, dry piping with joints tightly butted.

2.
Adhere 'factory applied vapor barrier jacket lap' smoothly and securely at longitudinal laps with a white vapor barrier adhesive.  Adhere 3 inch wide self-sealing butt joint strips over end joints.

3.
Fittings, Valves, & Accessories -

a.
Insulate with same type and thickness of insulation as pipe, with ends of insulation tucked snugly into throat of fitting and edges adjacent to pipe insulation tufted and tucked in.

b.
Cover insulation with one piece fitting cover secured by stapling or taping ends to adjacent pipe covering.

c.
Alternate Method  -  Insulate fittings, valves, and accessories with one inch of insulating cement and vapor seal with two 1/8 inch wet coats of vapor barrier mastic reinforced with glass fabric extending 2 inches onto adjacent insulation.

4.
Pipe Hangers -

a.
Do not allow pipes to come in contact with hangers.

b.
Provide 16 ga by 6 inch long galvanized shields at each pipe hanger to protect pipe insulation from crushing by clevis hanger.

B.
Below Grade Piping  -  Slip underground pipe insulation onto pipe and seal butt joints.  Where slip-on technique is not possible, slit insulation, apply to pipe, and seal seams and joints.


END OF SECTION

Project Number
1
15083

Project Name
Project Date
Potable Water Pipe Insulation


