
SECTION  15531
Supplement - 15531


ELECTRIC FURNACES
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  1 May 1996

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnish and install furnaces as described in Contract Documents.

B.
Related Sections

1.
Section 15055  -  General Mechanical Requirements

2.
Section 15861  -  Air Filters

PART 2 PRODUCTS
 2.1
MANUFACTURED UNITS
A.
Furnaces

1.
Factory assembled unit, UL listed with blower, heaters, steel casing, and completely wired.

2.
Cabinet  -  22 gauge minimum cold rolled steel with baked enamel finish.  Interior of cabinet around electric heating elements shall be lined with 1/2 inch thick 1-1/2 lb density fiberglass insulation.

3.
Blower -

a.
Centrifugal type, dynamically and statically balanced.

b.
Unit shall be belt driven or direct drive.

c.
Direct driven blower shall have a factory installed and wired speed controller providing at least three blower speeds.

4.
Heaters -

a.
Nickel-chrome and staged.

b.
Each set of heaters shall be equipped with limit control with fixed temperature 'OFF' setting and automatic reset with supplemental thermal cut-off safety fuses.

c.
Provide fan time-delay relay and circuit breakers.

d.
Furnaces shall have manually reset transformer.

e.
Provide at least two stages.

5.
Approved Manufacturers -

a.
Carrier

b.
Day & Night

c.
Trane

PART 3 EXECUTION  -  Not Used


END OF SECTION

ADVANCE \d252
B L A N K   P A G E

Project Number
1
15531

Project Name
Project Date
Electric Furnaces


