
SECTION  15744
Master - 15744


SPLIT SYSTEM HEAT PUMP UNITS
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  1 Nov 1996

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnish and install heat pumps as described in Contract Documents.

B.
Related Sections

1.
Division 03  -  Concrete pads

2.
Section 15055  -  General Mechanical Requirements

 1.2
SUBMITTALS
A.
Quality Assurance/Control  -  Equipment check-out sheets.

 1.3
QUALITY ASSURANCE
A.
Requirements of Regulatory Agencies  -  Each unit shall be UL or ETL labeled.

 1.4
WARRANTY
A.
Special Warranty  -  Provide five year warranty on compressors beginning from date of start-up.  Record start-up date on warranty certificate for each unit.

PART 2 PRODUCTS
 2.1
MANUFACTURED UNITS
A.
Heat Pumps

1.
Indoor Units -

a.
Compact wall mounted units.

b.
Supplementary electric heater, size as scheduled.

c.
Cabinet Finish as selected by Architect.

d.
Isolate moving parts from cabinets to reduce noise.

2.
Outdoor Units -

a.
Compressor shall be of rotary or scroll design.

b.
Fans shall be direct driven and discharge horizontally.

c.
Casing shall be fully weatherproof for outdoor installations.

d.
Microprocessor Controls shall be factory wired with field installed remote pendant station.

e.
Refrigerant shall be R-22.

f.
Isolate moving parts from cabinets to reduce noise.

g.
Use dry-charged tubing for connection of unit's refrigerant system.

3.
Approved Manufacturers – Model as approved by Architect (Design information per drawings)

a.
Carrier

b.
Friedrich

c.
Mitsubishi Electric

d.
Sanyo

PART 3 EXECUTION
 3.1
FIELD QUALITY CONTROL
A.
Manufacturer's Field Service  -  Units shall be started up, checked out, and adjusted by Unit Manufacturer's authorized factory trained service mechanic.  Use equipment check-out sheet provided by Manufacturer.  Complete and sign all items on sheet.


END OF SECTION

Project Number
1
15744

Project Name
Project Date
Split System Heat Pump Units


