
SECTION  15817
Supplement - 15817


UNDERGROUND DUCTWORK
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Mechanical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  4 Sep 1997

If there is any possibility of ground water level being above the bottom of underground ducts, do not use underground ducts.

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnish and install underground ductwork as described in Contract Documents.

B.
Related Sections

1.
Section 15055  -  General Mechanical Requirements

 1.2
REFERENCES
Delete or add references based on editing of other parts of this Section.

A.
American Society For Testing And Materials

1.
ASTM A 653-96, 'Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process'

 1.3
QUALITY ASSURANCE
A.
Pre-Installation Meeting  -  Participate in meeting specified in Section 03313.

PART 2 PRODUCTS
 2.1
COMPONENTS
A.
Ductwork

1.
Fiberglass-reinforced plastic duct system by Peabody Spunstrand Inc, Seattle, WA  98109  (206) 282-5449

2.
PVS or PVC coated galvanized steel duct with 4 mil thick coating on outside and on inside.

a.
Duct shall have and bear mark of approval of building code in authority for this Project.

b.
Gauges shall be as follows and be marked on each duct section.  Corrugate ducts 14 inches in diameter and larger.

  Size

  
   Gauge
 4 to 8 inches

26

 9 to 12 inches

24

14 to 22 inches

22

24 to 28 inches

20

30 to 40 inches

18

B.
Accessories

1.
Joint Sleeves  -  Galvanized sheet metal, galvanizing meeting requirements of ASTM A 527, G 60.

   Size

Gauge
Width
 4 to 12 inches
  26

4 inches

14 to 24 inches
  24

4 inches

26 to 36 inches
  22

6 inches

2.
Metal Boots  -  20 gauge galvanized steel, galvanizing meeting requirements of ASTM A 527, G 60.

3.
Connection Tape -

a.
Spunstrand  -  Sealtite PS401 sealing tape by Spunstrand Inc.

b.
Coated Steel  -  Hardcast tape with Hardcast RTA-50 adhesive

PART 3 EXECUTION
 3.1
INSTALLATION
A.
Spunstrand

1.
Join duct sections with galvanized sheet metal sleeve inside of duct secured with sheet metal screws.

2.
Wipe joint area clean and apply one layer of tape.  Tape shall cover all screw heads.

3.
Construct sheet metal boot with 1-1/2 inch flange to fit against duct.  Attach boot with self-tapping sheet metal screws, pulling boot flange snug to duct surface and tape joints.  Tape shall cover screw heads.

4.
Encase boot completely in concrete, covering well around and below taped joint.

B.
Coated Steel Duct

1.
Install 6 mil polyethylene vapor barrier around duct.

2.
Fittings shall be PVS or PVC.

3.
Join duct sections, fittings, and boots with sheet metal screws as detailed on Drawings.

4.
Wrap duct connections, including boot connections to ducts, with 2 layers of specified tape installed in accordance with Manufacturer's recommendations.  Cover screw heads with tape.

5.
Encase boot completely in concrete, covering well around and below taped joint.

6.
Where PVS or PVC coating has been scratched, scuffed, or peeled during shipping or installation, cover exposed metal with coating compound recommended by Manufacturer and in accordance with his recommendations.


END OF SECTION

Project Number
1
15817

Project Name
Project Date
Underground Ductwork


