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SECTION  16532
Master - 16532


PACKAGED BATTERY SYSTEMS
Refer to the Construction Documents Directive for general editing procedures and for document coordination procedures.

See the Church Electrical Directives & Guidelines for additional information regarding the work of this Section.

UPDATE  -  20 Oct 1997

20 Oct 97 -
Revised product specification format to comply with Section 01600.

PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnish and install fluorescent emergency lighting packs as described in Contract Documents.

B.
Related Sections

1.
Section 16055  -  General Electrical Requirements

PART 2 PRODUCTS
 2.1
EQUIPMENT
A.
Lighting Packs

1.
Shall operate one lamp at approximately 600 lumens initially and not less than 450 lumens after 90 minutes.

2.
Battery shall be long life nickel cadmium type.  Charger shall be capable of full recharge in 24 hours.

3.
Unit shall be complete with charging indicator light and test switch.

4.
Acceptable Manufacturers & Models -

a.
Bodine  -  B70A

b.
Chloride  -  CFP841

c.
Lithonia  -  PS-500

d.
Iota  -  I-48

e.
Equal as approved by Architect before bidding.  See Section 01600.

PART 3 EXECUTION
 3.1
INSTALLATION
A.
Install fluorescent emergency lighting pack in ballast channel with charging indicator light and test switch mounted on fixture end, or visible and accessible through lens.

B.
Wire so unit can be tested with lights on.

C.
Wire so lamps in normal mode are switched off with other lighting in area.  Connect emergency lighting unit to unswitched conductor of normal lighting circuit.


END OF SECTION

ADVANCE \d252
B L A N K   P A G E

Project Number
1
16532

Project Name
Project Date
Packaged Battery Systems


