Copyright 1999 AIA
MASTERSPEC
12/99


Copyright 1999, The American Institute of Architects (AIA)

SECTION 16124 - MEDIUM-VOLTAGE CABLES

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes cables and related splices, terminations, and accessories for medium-voltage electrical distribution systems.

1.3 SUBMITTALS

A. Product Data:  For each type of cable indicated.  Include splices and terminations for cables and cable accessories.

B. Samples:  16-inch (400-mm) lengths of each type of cable indicated.

Coordinate paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

C. Qualification Data:  For testing agency.

Delete test reports below if not required.

D. Source quality-control test reports.

Retain paragraph above or below.

E. Material Certificates:  For each cable and accessory type, signed by manufacturers, certifying that cables comply with requirements specified in Part 2 Article "Source Quality Control."

Delete below if Contractor is not required, in Part 3 "Field Quality Control" Article, to provide or perform field quality-control testing.

F. Field quality-control test reports.

1.4 QUALITY ASSURANCE

Edit paragraph below to include certification that may be specific to Project location.

A. Installer:  Engage a cable splicer, trained and certified by splice material manufacturer, to install, splice, and terminate medium-voltage cable.

Retain first paragraph and subparagraph below if independent testing agency is required in Part 3 "Field Quality Control" Article.

B. Testing Agency Qualifications:  Testing agency as defined by OSHA in 29 CFR 1910.7 or a member company of the InterNational Electrical Testing Association and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise testing specified in Part 3.

C. Source Limitations:  Obtain cables and accessories through one source from a single manufacturer.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

Edit below to suit Project.  See Editing Instruction No. 2 in the Evaluations.

E. Comply with IEEE C2 and NFPA 70.

1.5 PROJECT CONDITIONS

Delete paragraph below if no existing utilities.  Coordinate with requirements specified in Division 1 Section "Temporary Facilities and Controls" for temporary utilities.

A. Existing Utilities:  Do not interrupt utilities serving facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary utility services according to requirements indicated:

Edit first subparagraph below to suit Project.

1. Notify Architect at least two days in advance of proposed utility interruptions.

2. Do not proceed with utility interruptions without Architect's written permission.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain list of manufacturers and products below with either paragraph above.

1. Cables:

a. American Insulated Wire Corp.; a Leviton Company.

b. BICC Brand-Rex Company.

c. General Cable Corporation.

d. Kerite Co. (The); Hubbell Incorporated.

e. Okonite Company (The).

f. Pirelli Cables & Systems NA.

g. Rome Cable Corporation.

h. Southwire Company.

i. <Insert manufacturer's name.>

2. Cable Splicing and Terminating Products and Accessories:

a. Engineered Products Co.

b. G&W Electric Co.

c. MPHusky.

d. Raychem Corp.; Telephone Energy and Industrial Division.

e. RTE Components; Cooper Power Systems, Inc.

f. Scott Fetzer Co. (The); Adalet, Inc.

g. Thomas & Betts Corporation.

h. Thomas & Betts/Elastimold.

i. 3M Company; Electrical Products Division.

j. <Insert manufacturer's name.>

2.2 CABLES

A. Cable Type:  MV-90.

B. Conductor:  [Copper] [Aluminum].

C. Conductor Stranding:  [Compact round, concentric lay, Class B)] [Concentric lay, Class B].

Delete paragraph below if strand filling is not required for Project.

D. Strand Filling:  Conductor interstices are filled with impermeable compound.

See Editing Instruction No. 3 in the Evaluations for a discussion about insulation options in first two paragraphs and associated subparagraphs below.

E. Conductor Insulation:  Crosslinked polyethylene complying with [AEIC CS 5] [NEMA WC 7].

Retain paragraph above or below.

F. Conductor Insulation:  Ethylene-propylene rubber complying with [AEIC CS 6] [NEMA WC 8].

Retain two subparagraphs below with either paragraph above.  These options are cable voltage ratings, not system voltages.

1. Voltage Rating:  [5] [8] [15] [25] [35] kV.

2. Insulation Thickness:  [100] [133] percent insulation level.

Delete two paragraphs below for unshielded cable.  For shielded cable, select and edit first paragraph or select second.  See Editing Instruction No. 4 in the Evaluations.

G. Shielding:  [Copper tape] [Solid copper wires], helically applied over semiconducting insulation shield.

H. Shielding and Jacket:  Corrugated copper drain wires embedded in extruded, chlorinated, polyethylene jacket.

For "triplexed" single-conductor cable, retain paragraph below with or without ground conductors; otherwise, delete.

I. Three-Conductor Cable Assembly:  Three insulated, shielded conductors cabled together[ with ground conductors].

Edit subparagraph below for multiconductor cable.

1. Circuit Identification:  Color-coded tape (black, red, blue) under the metallic shielding.

Delete paragraph below except where single or multiconductor cable construction requires armor outer finish (Type MC).

J. Cable Armor:  [Interlocked aluminum] [Interlocked galvanized steel] [Corrugated aluminum tube] applied over cable.

Jackets can be applied over insulation or armor.

K. Cable Jacket:  [Sunlight-resistant PVC] [Crosslinked polyethylene] [Chlorosulfonated polyethylene].

2.3 SPLICE KITS

A. Connectors and Splice Kits:  Comply with IEEE 404; type as recommended by cable or splicing kit manufacturer for the application.

B. Splicing Products:  As recommended, in writing, by splicing kit manufacturer for specific sizes, ratings, and configurations of cable conductors.  Include all components required for complete splice, with detailed instructions.

Delete subparagraphs below not required.

1. Combination tape and cold-shrink-rubber sleeve kit with rejacketing by cast-epoxy-resin encasement or other waterproof, abrasion-resistant material.

2. Heat-shrink splicing kit of uniform, cross-section, polymeric construction with outer heat-shrink jacket.

3. Premolded, cold-shrink-rubber, in-line splicing kit.

4. Premolded EPDM splicing body kit with cable joint sealed by interference fit of mating parts and cable.

2.4 SOLID TERMINATIONS

Select from three paragraphs and associated subparagraphs below.

A. Multiconductor Cable Sheath Seals:  Type recommended by seal manufacturer for type of cable and installation conditions, including orientation.

Delete subparagraph below except for Type MC cable.

1. Compound-filled, cast-metal body, metal-clad cable terminator for metal-clad cable [with] [without] external plastic jacket.

Retain one of three subparagraphs below.

2. Cold-shrink sheath seal kit with preformed sleeve openings sized for cable and insulated conductors.

3. Heat-shrink sheath seal kit with phase- and ground-conductor rejacketing tubes, cable-end sealing boot, and sealing plugs for unused ground-wire openings in boot.

4. Cast-epoxy-resin sheath seal kit with wraparound mold and packaged, two-part, epoxy-resin casting material.

B. Shielded-Cable Terminations:  Comply with the following classes of IEEE 48.  Insulation class is equivalent to that of cable.  Include shield ground strap for shielded cable terminations.

Retain one or more of six subparagraphs below or revise to suit Project.

1. Class 1 Terminations:  Modular type, furnished as a kit, with stress-relief tube; multiple, molded-silicone rubber, insulator modules; shield ground strap; and compression-type connector.

2. Class 1 Terminations:  Heat-shrink type with heat-shrink inner stress control and outer nontracking tubes; multiple, molded, nontracking skirt modules; and compression-type connector.

3. Class 1 Terminations:  Modular type, furnished as a kit, with stress-relief shield terminator; multiple-wet-process, porcelain, insulator modules; shield ground strap; and compression-type connector.

4. Class 1 Terminations, Indoors:  Kit with stress-relief tube, nontracking insulator tube, shield ground strap, compression-type connector, and end seal.

5. Class 2 Terminations, Indoors:  Kit with stress-relief tube, nontracking insulator tube, shield ground strap, and compression-type connector.  Include silicone-rubber tape, cold-shrink-rubber sleeve, or heat-shrink plastic-sleeve moisture seal for end of insulation whether or not supplied with kits.

6. Class 3 Terminations:  Kit with stress cone and compression-type connector.

C. Nonshielded-Cable Terminations:  Kit with compression-type connector.  Include silicone-rubber tape, cold-shrink-rubber sleeve, or heat-shrink plastic-sleeve moisture seal for end of insulation whether or not supplied with kits.

2.5 SEPARABLE INSULATED CONNECTORS

Edit paragraph below to ensure that elbow-type terminators at equipment such as substations, transformers, and switchgear mate with bushing terminals in equipment.

A. Description:  Modular system, complying with IEEE 386, with disconnecting, single-pole, cable terminators and with matching, stationary, plug-in, dead-front terminals designed for cable voltage and for sealing against moisture.

Delete paragraph below unless terminations take the place of splices at cable junctions, such as in manholes and cable vaults.

B. Terminations at Distribution Points:  Modular type, consisting of terminators installed on cables and modular, dead-front, terminal junctions for interconnecting cables.

Delete three paragraphs below if not required.  Delete test-point feature for load-break unit if not required.

C. Load-Break Cable Terminators:  Elbow-type units with 200-A load make/break and continuous-current rating; coordinated with insulation diameter, conductor size, and material of cable being terminated.  Include test point on terminator body that is capacitance coupled.

D. Dead-Break Cable Terminators:  Elbow-type unit with 600-A continuous-current rating; designed for de-energized disconnecting and connecting; coordinated with insulation diameter, conductor size, and material of cable being terminated.  Include test point on terminator body that is capacitance coupled.

E. Dead-Front Terminal Junctions:  Modular bracket-mounted groups of dead-front stationary terminals that mate and match with above cable terminators.  Two-, three-, or four-terminal units as indicated, with fully rated, insulated, watertight conductor connection between terminals and complete with grounding lug, manufacturer's standard accessory stands, stainless-steel mounting brackets, and attaching hardware.

Delete drain wire below if not required.

1. Protective Cap:  Insulating, electrostatic-shielding, water-sealing cap with drain wire.

2. Portable Feed-Through Accessory:  Two-terminal, dead-front junction arranged for removable mounting on accessory stand of stationary terminal junction.

3. Grounding Kit:  Jumpered elbows, portable feed-through accessory units, protective caps, test rods suitable for concurrently grounding three phases of feeders, and carrying case.

4. Standoff Insulator:  Portable, single dead-front terminal for removable mounting on accessory stand of stationary terminal junction.  Insulators suitable for fully insulated isolation of energized cable-elbow terminator.

Delete first paragraph below if fault indicators are not required.

F. Test-Point Fault Indicators:  Applicable current-trip ratings and arranged for installation in test points of load-break separable connectors, and complete with self-resetting indicators capable of being installed with shotgun hot stick and tested with test tool.

G. Tool Set:  Shotgun hot stick with energized terminal indicator, fault-indicator test tool, and carrying case.

2.6 ARC-PROOFING MATERIALS

Delete this Article if cables are not arc proofed.

A. Tape for First Course on Metal Objects:  10-mil- (250-micrometer-) thick, corrosion-protective, moisture-resistant, PVC pipe-wrapping tape.

B. Arc-Proofing Tape:  Fireproof tape, flexible, conformable, intumescent to 0.3 inch (8 mm) thick, compatible with cable jacket.

C. Glass-Cloth Tape:  Pressure-sensitive adhesive type, 1/2 inch (13 mm) wide.

2.7 FAULT INDICATORS

Coordinate first paragraph below with Drawings by indicating current-trip ratings and quantities.

A. Indicators:  Manual-reset fault indicator, arranged to clamp to cable sheath and provide a display after a fault has occurred in cable.  Instrument shall not be affected by heat, moisture, and corrosive conditions and shall be recommended by manufacturer for installation conditions.

B. Resetting Tool:  Designed for use with fault indicators, with moisture-resistant storage and carrying case.

2.8 SOURCE QUALITY CONTROL

Edit paragraph below for cable type specified.  NEMA WC 7 applies to crosslinked polyethylene insulation; NEMA WC 8 applies to ethylene-propylene-rubber insulation.

A. Test and inspect cables according to [NEMA WC 7] [NEMA WC 8] before shipping.

Retain below if strand-filled or sealed conductors are specified.

B. Test strand-filled cables for water-penetration resistance according to ICEA T-31-610, using a test pressure of 5 psig (35 kPa).

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install cables according to IEEE 576.

B. Pull Conductors:  Do not exceed manufacturer's recommended maximum pulling tensions and sidewall pressure values.

1. Where necessary, use manufacturer-approved pulling compound or lubricant that will not deteriorate conductor or insulation.

2. Use pulling means, including fish tape, cable, rope, and basket-weave cable grips that will not damage cables and raceways.  Do not use rope hitches for pulling attachment to cable.

C. Install exposed cables parallel and perpendicular to surfaces of exposed structural members and follow surface contours where possible.

D. Support cables according to Division 16 Section "Basic Electrical Materials and Methods."

E. Install direct-buried cables on leveled and tamped bed of 3-inch- (75-mm-) thick, clean sand.  Separate cables crossing other cables or piping by a minimum of 4 inches (100 mm) of tamped earth.  Install permanent markers at ends of cable runs, changes in direction, and buried splices.

F. Install "buried-cable" warning tape 12 inches (305 mm) above cables.

G. In manholes, handholes, pull boxes, junction boxes, and cable vaults, train cables around walls by the longest route from entry to exit and support cables at intervals adequate to prevent sag.

Revise first paragraph below if separable insulated connectors are used.

H. Install cable splices at pull points and elsewhere as indicated; use standard kits.

I. Install terminations at ends of conductors and seal multiconductor cable ends with standard kits.

Coordinate paragraph and associated subparagraphs below with Drawings by indicating locations of separable insulated connectors.

J. Install separable insulated-connector components as follows:

1. Protective Cap:  At each terminal junction, with one on each terminal to which no feeder is indicated to be connected.

2. Portable Feed-Through Accessory:  Three.

3. Standoff Insulator:  Three.

Delete first paragraph and associated subparagraphs below if cables are not arc proofed.

K. Arc Proofing:  Unless otherwise indicated, arc proof medium-voltage cable at locations not protected by conduit, cable tray, direct burial, or termination materials.  In addition to arc-proofing tape manufacturer's written instructions, apply arc proofing as follows:

1. Clean cable sheath.

2. Wrap metallic cable components with 10-mil (250-micrometer) pipe-wrapping tape.

3. Smooth surface contours with electrical insulation putty.

4. Apply arc-proofing tape in one half-lapped layer with coated side toward cable.

5. Band arc-proofing tape with 1-inch- (25-mm-) wide bands of half-lapped, adhesive, glass-cloth tape 2 inches (50 mm) o.c.

L. Seal around cables passing through fire-rated elements according to Division 7 Section "Through-Penetration Firestop Systems."

Coordinate first paragraph below with Drawings by indicating locations of fault indicators or edit paragraph to describe locations.

M. Install fault indicators on each phase where indicated.

N. Ground shields of shielded cable at terminations, splices, and separable insulated connectors.  Ground metal bodies of terminators, splices, cable and separable insulated-connector fittings, and hardware.

O. Identify cables according to Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]."

3.2 FIELD QUALITY CONTROL

Retain one of first three paragraphs below.

A. Testing:  Owner will engage a qualified testing agency to perform the following field quality-control testing:

B. Testing:  Engage a qualified testing agency to perform the following field quality-control testing:

C. Testing:  Perform the following field quality-control testing:

Retain subparagraphs below with any paragraph selected above.  Edit to suit Project.

1. After installing medium-voltage cables and before electrical circuitry has been energized, test for compliance with requirements.

See Editing Instruction No. 5 in the Evaluations for discussion about NETA testing.

2. Perform each electrical test and visual and mechanical inspection stated in NETA ATS, Section 7.3.2.  Certify compliance with test parameters.

D. Remove malfunctioning units, replace with new units, and retest as specified above.

END OF SECTION 16124

MEDIUM-VOLTAGE CABLES
16124 - 1

