Copyright 1996 AIA
MASTERSPEC
12/96


Copyright 1996, The American Institute of Architects (AIA)

SECTION 16140 - WIRING DEVICES

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes receptacles, connectors, switches, and finish plates.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited for Project.

A. GFCI:  Ground-fault circuit interrupter.

B. TVSS:  Transient voltage surge suppressor.

1.4 SUBMITTALS

A. Product Data:  For each product specified.

B. Shop Drawings:  Legends for receptacles and switch plates.

Include sample review below if products may have critical features needing hands-on appraisal.

C. Samples:  For devices and device plates for color selection and evaluation of technical features.

D. Maintenance Data:  For materials and products to include in maintenance manuals specified in Division 1.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction.

B. Comply with NEMA WD 1.

C. Comply with NFPA 70.

1.6 COORDINATION

Delete paragraph below unless receptacles for Owner-Furnished equipment with plugs have unknown configurations.

A. Receptacles for Owner-Furnished Equipment:  Match plug configurations.

Delete below if cord and plug sets are not specified in Part 2.

1. Cord and Plug Sets:  Match equipment requirements.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.  Deliver extra materials to Owner.

Revise subparagraph below to suit Project.

1. Telephone/Power Service Poles:  One for each 10, but not less than one.

2. Floor Service-Outlet Assemblies:  One for each 10, but not less than one.

3. Poke-through, Fire-Rated Closure Plugs:  One for each five floor service outlets installed, but not less than two.

4. TVSS Receptacles:  One for each eight installed, but not less than two.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1. Wiring Devices:

a. Bryant Electric, Inc.

b. Eagle Electric Manufacturing Co., Inc.

c. GE Company; GE Wiring Devices.

d. Hubbell, Inc.; Wiring Devices Div.

e. Killark Electric Manufacturing Co.

f. Leviton Manufacturing Co., Inc.

g. Pass & Seymour/Legrand; Wiring Devices Div.

h. Pyle-National, Inc.; an Amphenol Co.

2. Wiring Devices for Hazardous (Classified) Locations:

a. Crouse-Hinds Electrical Co.; Distribution Equipment Div.

b. Killark Electric Manufacturing Co.

c. Pyle-National, Inc.; an Amphenol Co.

3. Multioutlet Assemblies:

a. Airey-Thompson Co.

b. Wiremold.

4. Poke-through, Floor Service Outlets and Telephone/Power Poles:

a. American Electric.

b. Hubbell, Inc.; Wiring Devices Div.

c. Pass & Seymour/Legrand; Wiring Devices Div.

d. Square D Co.

e. Wiremold.

2.2 RECEPTACLES

Select one of three paragraphs below to specify grade of receptacles.  See Editing Instruction No. 3 in the Evaluations for wiring device grades.

A. Straight-Blade and Locking Receptacles:  Heavy-Duty grade.

B. Straight-Blade and Locking Receptacles:  General-Duty grade.

C. Straight-Blade Receptacles:  Hospital grade.

Termination-type GFCI unit may be substituted for feed-through type where no protection of downstream receptacles is required.

D. GFCI Receptacles:  Feed-through type, with integral NEMA WD 6, Configuration 5-20R duplex receptacle arranged to protect connected downstream receptacles on same circuit.  Design units for installation in a 2-3/4-inch- (70-mm-) deep outlet box without an adapter.

E. Isolated-Ground Receptacles:  Equipment grounding contacts connected only to the green grounding screw terminal of the device with inherent electrical isolation from mounting strap.

1. Devices:  Listed and labeled as isolated-ground receptacles.

2. Isolation Method:  Integral to receptacle construction and not dependent on removable parts.

See Editing Instruction No. 4 in the Evaluations for data on device ratings.

F. TVSS Receptacles:  Duplex type, NEMA WD 6, Configuration 5-20R, with integral TVSS in line to ground, line to neutral, and neutral to ground.

1. TVSS Components:  Multiple metal-oxide varistors; rated a nominal clamp level of 500 transient-suppression voltage and minimum single transient pulse energy dissipation of 140 J line to neutral, and 70 J line to ground and neutral to ground.

2. Active TVSS Indication:  Light visible in face of device to indicate device as "active" or "no longer active."

3. Identification:  Distinctive marking on face of device denotes TVSS-type unit.

G. Industrial Heavy-Duty Receptacle:  Comply with IEC 309-1.

H. Hazardous (Classified) Location Receptacles:  Comply with NEMA FB 11.

2.3 PENDANT CORD/CONNECTOR DEVICES

Revise NEMA configuration to suit application.  Delete external cable grip where not required.

A. Description:  Matching, locking type, plug and receptacle body connector, NEMA WD 6, Configurations L5-20P and L5-20R, Heavy-Duty grade.

1. Body:  Nylon with screw-open cable-gripping jaws and provision for attaching external cable grip.

2. External Cable Grip:  Woven wire-mesh type made of high-strength galvanized-steel wire strand, matched to cable diameter, and with attachment provision designed for corresponding connector.

2.4 CORD AND PLUG SETS

Delete below unless required cord and plug sets for equipment are furnished by Owner or specified in other Sections.  Coordinate with other Sections and with Part 3 of this Section.

A. Description:  Match voltage and current ratings and number of conductors to requirements of equipment being connected.

1. Cord:  Rubber-insulated, stranded-copper conductors, with type SOW-A jacket.  Green-insulated grounding conductor, and equipment-rating ampacity plus a minimum of 30 percent.

2. Plug:  Nylon body and integral cable-clamping jaws.  Match cord and receptacle type for connection.

2.5 SWITCHES

Select one of two paragraphs below.

A. Snap Switches:  Heavy-duty, quiet type.

B. Snap Switches:  General-duty, quiet type.

C. Combination Switch and Receptacle:  Both devices in a single gang unit with plaster ears and removable tab connector that permit separate or common feed connection.

1. Switch:  20 A, 120/277-V ac.

2. Receptacle:  NEMA WD 6, Configuration 5-15R.

D. Dimmer Switches:  Modular, full-wave, solid-state units with integral, quiet on/off switches and audible and electromagnetic noise filters.

Modify subparagraph below to suit preference.

1. Control:  Continuously adjustable slide, toggle, or rotary knob.  Single-pole or three-way switch to suit connections.

2. Incandescent Lamp Dimmers:  Modular, 120 V, 60 Hz with continuously adjustable rotary knob, toggle, or slide; single pole with soft tap or other quiet switch; electromagnetic filter to eliminate noise, RF, and TV interference; and 5-inch (130-mm) wire connecting leads.

Use fluorescent dimmer switches below with compatible dimming-type ballasts.  Coordinate with Division 16 Section "Interior Lighting."  Use uniform ballast and lamp types to obtain consistent dimming characteristics.

3. Fluorescent Lamp Dimmers:  Modular; compatible with dimmer ballasts; trim potentiometer to adjust low-end dimming; dimmer-ballast combination capable of consistent dimming to a maximum of 1 percent of full brightness.

2.6 WALL PLATES

A. Single and combination types match corresponding wiring devices.

1. Plate-Securing Screws:  Metal with head color to match plate finish.

Select one of five subparagraphs below.  Coordinate with Division 9 Section "Painting."

2. Material for Finished Spaces:  Steel with wrinkled finish, white baked enamel, suitable for field painting.

3. Material for Finished Spaces:  0.04-inch- (1-mm-) thick, Type 302, satin-finished stainless steel.

4. Material for Finished Spaces:  0.04-inch- (1-mm-) thick brushed brass with factory polymer finish.

5. Material for Finished Spaces:  0.04-inch- (1-mm-) thick brass, satin chrome-plated.

6. Material for Finished Spaces:  0.05-inch- (1.2-mm-) thick anodized aluminum.

Select one of three subparagraphs below or delete all.

7. Material for Unfinished Spaces:  Galvanized steel.

8. Material for Unfinished Spaces:  Ribbed plastic.

9. Material for Unfinished Spaces:  Smooth plastic.

2.7 FLOOR SERVICE FITTINGS

Items in this Article are available for telephone and data cable service as well as power.  Edit to suit Project.

Select one of three paragraphs below.

A. Type:  Modular, flush-type, dual-service units suitable for wiring method used.

B. Type:  Modular, pop-up, dual-service units suitable for wiring method used.

C. Type:  Modular, above-floor, dual-service units suitable for wiring method used.

D. Compartmentation:  Barrier separates power and signal compartments.

E. Housing Material:  Die-cast aluminum, satin finished.

F. Power Receptacle:  NEMA WD 6, Configuration 5-20R, gray finish, unless otherwise indicated.

G. Signal Outlet:  Blank cover with bushed cable opening, unless otherwise indicated.

2.8 POKE-THROUGH ASSEMBLIES

Delete this Article if poke-through assembly devices are specified in another Section.  Use below with "Floor Service Fittings" Article above.

A. Description:  Factory-fabricated and -wired assembly of below-floor junction box unit with multichanneled, through-floor raceway/firestop unit and detachable matching floor service-outlet assembly.

1. Size:  Selected to fit nominal 3-inch (75-mm) cored holes in floor and matched to floor thickness.

Revise subparagraph below to coordinate with fire ratings.

2. Fire Rating:  Unit is listed and labeled for fire rating of floor-ceiling assembly.

3. Closure Plug:  Arranged to close unused 3-inch (75-mm) cored openings and reestablish fire rating of floor.

4. Wiring:  Three No. 12 AWG power and ground conductors; one 75-ohm coaxial telephone/data cable; and one four-pair, 75-ohm telephone/data cable.

2.9 MULTIOUTLET ASSEMBLIES

If not indicated on Drawings, add mounting heights, raceway sizes, and types and spacing of receptacle devices to paragraph below.  Add descriptions of special features in assemblies, such as fused receptacles, special-purpose switches, and channels for communication wiring.

A. Components of Assemblies:  Products from a single manufacturer designed for use as a complete, matching assembly of raceways and receptacles.

Some finish options may be available from manufacturers.  Edit to suit Project.  Select one of two paragraphs below.

B. Raceway Material:  Metal, with manufacturer's standard finish.

C. Raceway Material:  Nonmetal.

D. Wire:  No. 12 AWG.

2.10 TELEPHONE/POWER SERVICE POLES

A. Description:  Factory-assembled and -wired units to extend power, telephone, and data service from distribution wiring concealed in ceiling to devices or outlets in pole near floor.

1. Poles:  Nominal 2.5-inch- (65-mm-) square cross section with height adequate to extend from floor to at least 6 inches (150 mm) above ceiling, and separate channels for power and signal wiring.

2. Mounting:  Ceiling trim flange with concealed bracing arranged for positive connection to ceiling supports, and pole foot with carpet pad attachment.

Specify final finish, if known.

3. Finishes:  One of manufacturers standard finish and trim combinations, including painted and satin anodized-aluminum finishes and wood-grain-type trim.

Coordinate three subparagraphs below with Division 16 Section "Premises Telephone Wiring."

4. Wiring:  Sized for three No. 12 AWG power and ground conductors; one 75-ohm coaxial telephone/data cable; and one four-pair, 75-ohm telephone/data cable.

5. Power Receptacles:  Two single; 20-A; heavy-duty; NEMA WD 6, Configuration 5-20R units.

6. Signal Outlets:  Blank insert with bushed cable opening.

2.11 FINISHES

See Editing Instruction No. 2 in the Evaluations for a discussion of wiring device colors.  Select one of five paragraphs below and revise to suit Project.  Coordinate with Drawings.

A. Color:  Ivory, unless otherwise indicated or required by Code.

B. Color:  Brown, unless otherwise indicated or required by Code.

C. Color:  Gray, unless otherwise indicated or required by Code.

D. Color:  White, unless otherwise indicated or required by Code.

E. Color:  Manufacturers standard, as selected by Architect.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install devices and assemblies plumb and secure.

B. Install wall plates when painting is complete.

C. Install wall dimmers to achieve indicated rating after derating for ganging as instructed by manufacturer.

D. Do not share neutral conductor on load side of dimmers.

Coordinate two paragraphs below with Drawings.

E. Arrangement of Devices:  Unless otherwise indicated, mount flush, with long dimension vertical, and grounding terminal of receptacles on top.  Group adjacent switches under single, multigang wall plates.

F. Protect devices and assemblies during painting.

G. Adjust locations at which floor service outlets and telephone/power service poles are installed to suit arrangement of partitions and furnishings.

3.2 IDENTIFICATION

A. Comply with Division 16 Section "Electrical Identification."

Select paragraph above or below.

B. Comply with Division 16 Section "Basic Electrical Materials and Methods."

1. Switches:  Where three or more switches are ganged, and elsewhere as indicated, identify each switch with approved legend engraved on wall plate.

2. Receptacles:  Identify panelboard and circuit number from which served.  Use machine-printed, pressure-sensitive, abrasion-resistant label tape on face of plate and durable wire markers or tags within outlet boxes.

3.3 CONNECTIONS

A. Connect wiring device grounding terminal to outlet box with bonding jumper.

Select paragraph above or below.  Coordinate with Division 16 Section "Grounding."

B. Connect wiring device grounding terminal to branch-circuit equipment grounding conductor.

C. Isolated-Ground Receptacles:  Connect to isolated-ground conductor routed to designated isolated equipment ground terminal of electrical system.

D. Tighten electrical connectors and terminals according to manufacturers published torque-tightening values.  If manufacturers torque values are not indicated, use those specified in UL 486A and UL 486B.

3.4 FIELD QUALITY CONTROL

A. Test wiring devices for proper polarity and ground continuity.  Operate each device at least six times.

B. Check TVSS receptacle indicating lights for normal indication.

Delete paragraph below if GFCIs are not in Part 2.

C. Test GFCI operation with both local and remote fault simulations according to manufacturer's written instructions.

D. Replace damaged or defective components.

3.5 CLEANING

A. Internally clean devices, device outlet boxes, and enclosures.  Replace stained or improperly painted wall plates or devices.

END OF SECTION 16140

WIRING DEVICES
16140 - 1

