Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16140 - WIRING DEVICES

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes:

Adjust list below to suit Project.

1. Receptacles.

2. Connectors.

3. Switches.

4. Finish plates.

5. Multioutlet assemblies.

6. Poke-through floor service outlets and fittings.

7. Telephone/power poles.

1.2 SUBMITTALS

A. Product Data:  For each product indicated.

Retain first paragraph below if products have critical features needing hands-on appraisal.

B. Samples:  For devices, device plates, multioutlet assemblies, poke-through floor service outlets, and telephone/power poles for finish and color selection, and evaluation of technical features.

C. Field quality-control test reports.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NEMA WD 1.

C. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following

1. Wiring Devices:

a. Bryant Electric, Inc.

b. Eagle Electric Manufacturing Co., Inc.

c. GE Company; GE Wiring Devices.

d. Hubbell, Inc.; Wiring Devices Div.

e. Killark Electric Manufacturing Co.

f. Leviton Manufacturing Co., Inc.

g. Pass & Seymour/Legrand; Wiring Devices Div.

h. Pyle-National, Inc.; an Amphenol Co.

i. <Insert manufacturer.>

2. Multioutlet Assemblies:

a. Airey-Thompson Co.

b. Wiremold.

c. <Insert manufacturer.>

3. Poke-through Assemblies, Floor Service Outlets and Telephone/Power Poles:

a. American Electric.

b. Hubbell, Inc.; Wiring Devices Div.

c. Pass & Seymour/Legrand; Wiring Devices Div.

d. Square D Co.

e. Wiremold.

f. <Insert manufacturer.>

2.2 RECEPTACLES

See Editing Instruction No. 3 in the Evaluations for wiring device grades.

A. Straight-Blade and Locking Receptacles:  [Heavy-Duty] [General-Duty] [Hospital] grade.

B. GFCI Receptacles:  Feed-through type, with integral NEMA WD 6, Configuration 5-20R duplex receptacle arranged to protect connected downstream receptacles on same circuit.  Design units for installation in a 2-3/4-inch- (70-mm-) deep outlet box without an adapter.

2.3 SWITCHES

A. Snap Switches:  [Heavy] [General]-duty, quiet type.

B. Dimmer Switches:  Modular, full-wave, solid-state units with integral, quiet on/off switches and audible and electromagnetic noise filters.

Modify first subparagraph below to suit preference.

1. Control:  Continuously adjustable [slide] [toggle] [or] [rotary knob].  Single-pole or three-way switch to suit connections.

2. Incandescent Lamp Dimmers:  Modular, 120 V, 60 Hz, single pole with soft tap or other quiet switch; electromagnetic filter to eliminate audible noise, and RF, and TV interference.

Use fluorescent dimmer switches below with compatible dimming-type ballasts.  Coordinate with Division 16 Section "Interior Lighting."  Use uniform ballast and lamp types to obtain consistent dimming characteristics.

3. Fluorescent Lamp Dimmers:  Modular; compatible with dimmer ballasts; trim potentiometer to adjust low-end dimming; dimmer-ballast combination capable of consistent dimming to a maximum of one percent of full brightness.

2.4 FINISH COLOR FOR RECEPTACLES AND SWITCHES

See Editing Instruction No. 2 in the Evaluations for a discussion of wiring device colors.Coordinate with Drawings.

A. Color:  [Ivory] [Brown] [Gray] [White] [Manufacturer's standard], unless otherwise indicated or required by Code.

2.5 WALL PLATES

A. Single and combination types match corresponding wiring devices.

1. Plate-Securing Screws:  Metal with head color to match plate finish.

Coordinate first subparagraph below with Division 9 Section "Painting."

2. Material for Finished Spaces:  [Steel with wrinkled finish, white baked enamel, suitable for field painting] [White nylon] [0.04-inch- (1-mm-) thick, Type 302, satin-finished stainless steel] [0.04-inch- (1-mm-) thick brass, satin chrome-plated].

3. Material for Unfinished Spaces:  [Galvanized steel] [White nylon] [Dark brown nylon].

2.6 FLOOR SERVICE FITTINGS

Items in this Article are available for telephone and data cable service as well as power.  Use with poke-through assemblies specified below.  Edit to suit Project.

A. Type:  Modular, [flush-type] [pop-up] [above-floor] dual-service units suitable for wiring method used.

B. Compartmentation:  Barrier separates power and signal compartments.

C. Housing Material:  Die-cast aluminum, satin finished.

D. Power Receptacle:  NEMA WD 6, Configuration 5-20R, gray finish, unless otherwise indicated.

E. Signal Outlet:  Blank cover with bushed cable opening, unless otherwise indicated.

2.7 POKE-THROUGH ASSEMBLIES

Delete this Article if poke-through assembly devices are specified in another Section.  Retain below with "Floor Service Fittings" Article.

A. Description:  Factory-fabricated and -wired assembly of below-floor junction box unit with multichannel, through-floor raceway/firestop unit and detachable matching floor service-outlet assembly.

1. Size:  Selected to fit nominal 3-inch (75-mm) cored holes in floor and matched to floor thickness.

Revise first subparagraph below to coordinate with fire ratings.

2. Fire Rating:  Unit is listed for fire rating of floor-ceiling assembly.

3. Closure Plug:  Arranged to close unused 3-inch (75-mm) cored openings and reestablish fire rating of floor.

4. Minimum Wiring Capacity:  Three No. 12 AWG power and ground conductors; one 75-ohm coaxial telephone/data cable; and one four-pair, 75-ohm telephone/data cable.

2.8 MULTIOUTLET ASSEMBLIES

If not indicated on Drawings, add mounting heights, raceway sizes, and types and spacing of receptacle devices to paragraph below.  Add descriptions of special features in assemblies, such as fused receptacles, special-purpose switches, and channels for communication wiring.

A. Components of Assemblies:  Products from a single manufacturer designed for use as a complete, matching assembly of raceways and receptacles.

Some finish options may be available from manufacturers.  Edit first paragraph below to suit Project.

B. Raceway Material:  [Metal, with manufacturer's standard finish] [Nonmetal].

C. Wire:  No. 12 AWG.

2.9 TELEPHONE/POWER SERVICE POLES

A. Description:  Factory-assembled and -wired units to extend power, telephone, and data service from distribution wiring concealed in ceiling to devices or outlets in pole near floor.

1. Poles:  Nominal 2.5-inch- (65-mm-) square cross section with height adequate to extend from floor to at least 6 inches (150 mm) above ceiling, and separate channels for power and signal wiring.

2. Mounting:  Ceiling trim flange with concealed bracing arranged for positive connection to ceiling supports, and pole foot with carpet pad attachment.

Specify final finish and trim, if known.

3. Finish:  <Insert one of manufacturer's standard finish and trim combinations.>

Coordinate three subparagraphs below with Division 16 Section "Premises Telephone Wiring."

4. Wiring:  Sized for three No. 12 AWG power and ground conductors; one 75-ohm coaxial telephone/data cable; and one four-pair, 75-ohm telephone/data cable.

5. Power Receptacles:  Two single; 20-A; heavy-duty; NEMA WD 6, Configuration 5-20R units.

6. Signal Outlets:  Blank insert with bushed cable opening.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install devices and assemblies plumb and secure.

B. Install wall plates when painting is complete.

C. Install wall dimmers to achieve indicated rating after derating for ganging as instructed by manufacturer.

D. Do not share neutral conductor on load side of dimmers.

Coordinate first two paragraphs below with Drawings.

E. Arrangement of Devices:  Unless otherwise indicated, mount flush, with long dimension vertical, and grounding terminal of receptacles on top.  Group adjacent switches under single, multigang wall plates.

F. Protect devices and assemblies during painting.

G. Adjust locations at which floor service outlets and telephone/power service poles are installed to suit arrangement of partitions and furnishings.

3.2 FIELD QUALITY CONTROL

A. Test wiring devices for proper polarity and ground continuity.  Operate each device at least six times.

B. Test GFCI operation with both local and remote fault simulations according to manufacturer's written instructions.

C. Replace damaged or defective components, and prepare written report of tests.

END OF SECTION 16140

WIRING DEVICES
16140 - 1

