Copyright 1997 AIA
MASTERSPEC
9/97


Copyright 1997, The American Institute of Architects (AIA)

SECTION 16145 - LIGHTING CONTROL DEVICES

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes time switches, photoelectric relays, occupancy sensors, and multipole lighting relays and contactors.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 13 Section "Lighting Controls" for low-voltage, manual and programmable lighting control systems.

2. Division 16 Section "Wiring Devices" for wall-box dimmers and manual light switches.

3. Division 16 Section "Dimming Controls" for architectural dimming system equipment.

1.3 SUBMITTALS

A. Product Data:  Include dimensions and data on features, components, and ratings for lighting control devices.

Retain paragraph below if products have critical features needing hands-on appraisal.

B. Samples:  Occupancy sensors for color selection and evaluation of technical features.

C. Field Test Reports:  Indicate and interpret test results for compliance with performance requirements.

D. Maintenance Data:  For lighting control devices to include in maintenance manuals specified in Division 1.

1.4 QUALITY ASSURANCE

Retain paragraph below if devices specified in this Section are to function with low-voltage lighting controls specified in another Section.  Edit to refer to relevant Section titles.

A. Source Limitations:  Obtain lighting control devices from a single source with total responsibility for compatibility of lighting control system components specified in this Section, in Division 13 Section "Lighting Controls," and in Division 16 Section "Dimming Controls."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, for their indicated use and installation conditions by a testing agency acceptable to authorities having jurisdiction.

C. Comply with 47 CFR 15, Subparts A and B, for Class A digital devices.

D. Comply with NFPA 70.

1.5 COORDINATION

Retain this Article if devices specified in this Section are to be interconnected with systems specified in other Sections.  Edit to refer to relevant Section titles.

A. Coordinate features of devices specified in this Section with systems and components specified in other Sections to form an integrated system of compatible components.  Match components and interconnections for optimum performance of specified functions.  Include coordination with the following:

Edit subparagraphs below to reference only Sections in this Project.

1. Division 13 Section "Lighting Controls."

2. Division 16 Section "Panelboards."

3. Division 16 Section "Dimming Controls."

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1. Contactors and Relays:

a. Automatic Switch Co.

b. Challenger Electrical Equipment Corp.

c. Cutler-Hammer Products; Eaton Corporation.

d. Furnas Electric Co.

e. GE Lighting Controls.

f. Hubbell Lighting, Inc.

g. Siemens Energy and Automation, Inc.

h. Square D Co.; Power Management Organization.

i. Zenith Controls, Inc.

2. Time Switches:

a. Diversified Electronics, Inc.

b. Grasslin Controls Corp.

c. Intermatic, Inc.

d. Leviton Manufacturing.

e. Paragon Electric Co., Inc.

f. Tork, Inc.

g. Zenith Controls, Inc.

3. Photoelectric Relays:

a. Allen-Bradley/Rockwell Automation.

b. Area Lighting Research, Inc.

c. Fisher Pierce.

d. Grasslin Controls, Corp.

e. Intermatic, Inc.

f. Paragon Electric Co., Inc.

g. Rhodes:  M H Rhodes, Inc.

h. SSAC, Inc.

i. Tork, Inc.

4. Occupancy Sensors:

a. Arrow Hart Wiring Devices.

b. BRK Electronics.

c. Bryant Electric.

d. Honeywell, Inc.; Home and Building Controls.

e. Hubbell Lighting, Inc.

f. Lightolier.

g. Lithonia Control Systems.

h. MyTech Corporation.

i. Novitas, Inc.

j. RAB Electric Manufacturing Co., Inc.

k. SenTec, Inc.

l. Sterner Lighting Systems, Inc.

m. Tork, Inc.

n. Touchplate.

o. Unenco Electronics (A Hubbell Co.).

p. Watt Stopper, Inc. (The).

2.2 GENERAL LIGHTING CONTROL DEVICE REQUIREMENTS

A. Line-Voltage Surge Protection:  Include in all 120- and 277-V solid-state equipment.  Comply with UL 1449 and with ANSI C62.41 for Category A locations.

2.3 TIME SWITCHES

Delete one or both paragraphs below.

A. Description:  Solid-state programmable units with alphanumeric display complying with UL 917.

B. Description:  Electromechanical-dial type complying with UL 917.

Retain, add, delete, or revise features listed in subparagraphs below to suit applications for time-switch type retained above.

1. Astronomic dial.

2. Two contacts, rated 30 A at 277-V ac, unless otherwise indicated.

3. Two pilot-duty contacts, rated 2 A at 240-V ac, unless otherwise indicated.

4. Eight-day program uniquely programmable for each weekday and holidays.

5. Skip-day mode.

2.4 PHOTOELECTRIC RELAYS

Retain, delete, or revise types and features below to suit Project.

A. Description:  Solid state, with single-pole, double-throw dry contacts rated to operate connected relay or contactor coils or microprocessor input, and complying with UL 773A.

B. Light-Level Monitoring Range:  0 to 3500 fc (0 to 37 673 lx), with an adjustment for turn-on/turn-off levels.

C. Time Delay:  Prevents false operation.

D. Indoor Ceiling- or Wall-Mounting Units:  Adjustable for turn-on/turn-off levels, semiflush, calibrated to detect adequacy of daylighting in perimeter locations, and arranged to turn artificial illumination on and off to suit varying intensities of available daylighting.

E. Indoor Skylight Units:  Housed in a threaded plastic fitting for mounting under skylight.

F. Outdoor Sealed Units:  Weathertight housing, resistant to high temperatures and equipped with sun-glare shield and ice preventer.

2.5 OCCUPANCY SENSORS

Coordinate first three paragraphs below with Drawings.  Select subparagraphs to specify various types of units required for Project.

Retain ceiling-mounting units below for units used independent of low-voltage lighting control system.

A. Ceiling-Mounting Units:  Unit receives control power from a separately mounted auxiliary power and control unit, and operates power switching contacts in that unit.

Retain ceiling-mounting units below for units used with a low-voltage lighting control system, usually a programmable system.

B. Ceiling-Mounting Units:  Unit receives 24-V dc power from a remote source and, on sensing occupancy, closes contacts that provide signal input to a remote microprocessor-based lighting control system.

Retain paragraph below for typical units mounted at wall-switch locations.

C. Switch-Box-Mounting Units:  Unit receives power directly from switch leg of the 120- or 277-V ac circuit it controls and operates integral power switching contacts rated 800 W at 120-V ac, and 1000 W at 277-V ac, minimum.

D. Operation:  Turns lights on when room or covered area is occupied and off when unoccupied, unless otherwise indicated.

1. Time Delay for Turning Lights Off:  Adjustable over a range from 1 to 15 minutes, minimum.

Feature below is usually available only on wall-switch units.

2. Manual Override Switch:  Turns lights off manually regardless of elapsed time delay.

Two subparagraphs below specify optional features.  Delete those not required.

3. Ambient-Light-Level Control:  Adjustable for setting a level of ambient illumination above which sensor will not turn lights on when occupancy is sensed.

For units used independent of programmable lighting control systems, optional feature below may be used to control HVAC system or energy-conservation features.  Coordinate with Drawings and with Specifications for HVAC system control and sequence of operation.  Occupancy sensors applied with programmable lighting control systems can achieve same functions through system programming.

4. Isolated Relay Contact:  Operates on detection of occupancy or vacancy, as indicated, to activate an independent function.

E. Auxiliary Power and Control Units:  As follows:

1. Relays rated for a minimum of 20-A normal ballast load or 13-A tungsten filament or high-inrush ballast load.

2. Sensor Power Supply:  Rated to supply the number of connected sensors.

Select from three paragraphs below specifying examples of different sensor types.  Edit sensitivity requirements and other features to suit individual applications, or define in a schedule.  Coordinate with Drawings.

F. Passive-Infrared Type:  Detects occupancy by a combination of heat and movement in zone of coverage.  Each sensor detects occupancy anywhere in an area of 1000 sq. ft. (93 sq. m) by detecting occurrence of 6-inch (150-mm) minimum movement of any portion of a human body that presents a minimum target of 36 sq. in. (232 sq. cm) to the sensor.

G. Ultrasonic Type:  Emits a beam of ultrasonic energy and detects occupancy through use of Doppler's principle in discerning movement in zone of coverage by sensing a change in pattern of reflected ultrasonic energy.

H. Dual-Technology Type:  Uses a combination of passive-infrared and ultrasonic detection methods to distinguish between occupied and unoccupied conditions for area covered.  Particular technology or combination of technologies that controls each function (on or off) is selectable in the field by operating controls on unit.

2.6 MULTIPOLE CONTACTORS AND RELAYS

A. Description:  Electrically operated and mechanically held, and complying with UL 508 and NEMA ICS 2.

Edit two subparagraphs below for specific ratings, if required, or indicate on Drawings.  Coordinate control voltage with low-voltage lighting control system if used.  Coordinate with Drawings.

1. Current Rating for Switching:  UL listing or rating consistent with type of load served, including tungsten filament, inductive, and high-inrush ballast (ballasts with 15 percent or less total harmonic distortion of normal load current).

2. Control Coil Voltage:  Match control power source.

PART 3 -  EXECUTION

3.1 INSTALLATION

Coordinate this Article with Drawings.

A. Install equipment level and plumb and according to manufacturer's written instructions.

B. Mount lighting control devices according to manufacturer's written instructions and requirements in Division 16 Section "Basic Electrical Materials and Methods."

C. Mounting heights indicated are to bottom of unit for suspended devices and to center of unit for wall-mounting devices.

3.2 CONTROL WIRING INSTALLATION

A. Install wiring between sensing and control devices according to manufacturer's written instructions and as specified in Division 16 Section "Conductors and Cables" for low-voltage connections and Division 16 Section "Voice and Data Systems" for digital circuits.

Delete one of two paragraphs below or specify an alternate wiring method, such as cable tray.

B. Wiring Method:  Install all wiring in raceway as specified in Division 16 Section "Raceways and Boxes."

C. Wiring Method:  Install all wiring in raceway as specified in Division 16 Section "Raceways and Boxes," unless run in accessible ceiling space and gypsum board partitions.

D. Bundle, train, and support wiring in enclosures.

E. Ground equipment.

F. Connections:  Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A.

3.3 IDENTIFICATION

A. Identify components and power and control wiring according to Division 16 Section "Basic Electrical Materials and Methods."

Retain paragraph above or below.

B. Identify components and power and control wiring according to Division 16 Section "Electrical Identification."

3.4 FIELD QUALITY CONTROL

A. Schedule visual and mechanical inspections and electrical tests with at least seven days' advance notice.

Delete nonapplicable items below.

B. Inspect control components for defects and physical damage, testing laboratory labeling, and nameplate compliance with the Contract Documents.

C. Check tightness of electrical connections with torque wrench calibrated within previous six months.  Use manufacturer's recommended torque values.

D. Verify settings of photoelectric devices with photometer calibrated within previous six months.

E. Electrical Tests:  Use particular caution when testing devices containing solid-state components.  Perform the following according to manufacturer's written instructions:

1. Continuity tests of circuits.

2. Operational Tests:  Set and operate devices to demonstrate their functions and capabilities in a methodical sequence that cues and reproduces actual operating functions.

a. Include testing of devices under conditions that simulate actual operational conditions.  Record control settings, operations, cues, and functional observations.

F. Correct deficiencies, make necessary adjustments, and retest.  Verify that specified requirements are met.

G. Test Labeling:  After satisfactory completion of tests and inspections, apply a label to tested components indicating test results, date, and responsible agency and representative.

H. Reports:  Written reports of tests and observations.  Record defective materials and workmanship and unsatisfactory test results.  Record repairs and adjustments.

3.5 CLEANING

A. Cleaning:  Clean equipment and devices internally and externally using methods and materials recommended by manufacturers, and repair damaged finishes.

3.6 DEMONSTRATION

Services covered in this Article are optional; retain if Project warrants.  Revise hours below to suit Project and system.  Coordinate with Division 1 training requirements.  If Project includes programmable lighting controls, coordinate with testing of that system.

A. Coordinate with training for low-voltage, programmable lighting control system specified in Division 13 Section "Lighting Controls."

B. Engage a factory-authorized service representative to train Owner's maintenance personnel as specified below:

1. Train Owner's maintenance personnel on troubleshooting, servicing, adjusting, and preventive maintenance.  Provide a minimum of three hours' training.

2. Training Aid:  Use the approved final version of maintenance manuals as a training aid.

3. Schedule training with Owner, through Architect, with at least seven days' advance notice.

3.7 ON-SITE ASSISTANCE

A. Occupancy Adjustments:  Within one year of date of Substantial Completion, provide up to three Project site visits, when requested, to adjust light levels, make program changes, and adjust sensors and controls to suit actual conditions.

END OF SECTION 16145

LIGHTING CONTROL DEVICES
16145 - 1

