Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16145 - LIGHTING CONTROL DEVICES

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Time switches.

2. Photoelectric relays.

3. Occupancy sensors.

4. Multipole lighting relays.

5. Multipole lighting contactors.

1.2 SUBMITTALS

A. Product Data:  For each type of lighting control device indicated.

B. Field quality-control test reports.

C. Operation and maintenance data.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with 47 CFR 15, Subparts A and B, for Class A digital devices.

C. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Contactors and Relays:

a. Automatic Switch Co.

b. Challenger Electrical Equipment Corp.

c. Cutler-Hammer Products; Eaton Corporation.

d. Furnas Electric Co.

e. GE Lighting Controls.

f. Hubbell Lighting, Inc.

g. Siemens Energy and Automation, Inc.

h. Square D Co.; Power Management Organization.

i. Zenith Controls, Inc.

j. <Insert manufacturer.>

2. Time Switches:

a. Diversified Electronics, Inc.

b. Grasslin Controls Corp.

c. Intermatic, Inc.

d. Leviton Manufacturing.

e. Paragon Electric Co., Inc.

f. Tork, Inc.

g. Zenith Controls, Inc.

h. <Insert manufacturer.>

3. Photoelectric Relays:

a. Allen-Bradley/Rockwell Automation.

b. Area Lighting Research, Inc.

c. Fisher Pierce.

d. Grasslin Controls, Corp.

e. Intermatic, Inc.

f. Paragon Electric Co., Inc.

g. Rhodes, M H , Inc.

h. SSAC, Inc.

i. Tork, Inc.

j. <Insert manufacturer.>

4. Occupancy Sensors:

a. Arrow Hart Wiring Devices.

b. BRK Electronics.

c. Bryant Electric.

d. Honeywell, Inc.; Home and Building Controls.

e. Hubbell Lighting, Inc.

f. Lightolier.

g. Lithonia Control Systems.

h. MyTech Corporation.

i. Novitas, Inc.

j. RAB Electric Manufacturing Co., Inc.

k. SenTec, Inc.

l. Sterner Lighting Systems, Inc.

m. Tork, Inc.

n. Touchplate.

o. Unenco Electronics (A Hubbell Co.).

p. Watt Stopper, Inc. (The).

q. <Insert manufacturer.>

2.2 GENERAL LIGHTING CONTROL DEVICE REQUIREMENTS

A. Line-Voltage Surge Protection:  Include in all 120- and 277-V solid-state equipment.  Comply with UL 1449 and with ANSI C62.41 for Category A locations.

2.3 TIME SWITCHES

A. Description:  [Solid-state programmable type with alphanumeric display] [Electromechanical-dial type] complying with UL 917.

Retain, add, delete, or revise features listed in subparagraphs below to suit applications.

1. Astronomic dial.

2. Two contacts, rated 30 A at 277-V ac, unless otherwise indicated.

3. Two pilot-duty contacts, rated 2 A at 240-V ac, unless otherwise indicated.

4. Eight-day program uniquely programmable for each weekday and holidays.

5. Skip-day mode.

2.4 PHOTOELECTRIC RELAYS

Retain, delete, or revise features in this Article to suit Project.

A. Outdoor Sealed Units:  Solid state, with single-pole, double-throw dry contacts rated to operate connected relay or contactor coils or microprocessor input, and complying with UL 773A Weathertight housing, resistant to high temperatures and equipped with sun-glare shield and ice preventer.

1. Light-Level Monitoring Range:  0 to 3500 fc (0 to 37 673 lx), with an adjustment for turn-on/turn-off levels.

2. Time Delay:  Prevents false operation.

2.5 OCCUPANCY SENSORS

A. Ceiling and Non-Switch-Box Mounting Units:  Unit receives control power from a separately mounted auxiliary power and control unit, and operates power switching contacts in that unit in response to signals from sensors.

1. Auxiliary Power and Control Units:  Matched to sensors with which used.  Features as follows:

a. Relays rated for a minimum of 20-A normal ballast load or 13-A tungsten filament or high-inrush ballast load.

b. Sensor Power Supply:  Rated to supply the number of connected sensors.

Retain first paragraph and subparagraph below for typical units mounted at wall-switch locations.

B. Switch-Box-Mounting Units:  Unit receives power directly from switch leg of the 120- or 277-V ac circuit it controls and operates integral power switching contacts rated 800 W at 120-V ac, and 1000 W at 277-V ac, minimum.

1. Manual Override Switch:  Turns lights off manually regardless of elapsed time delay.

C. Operation:  Turns lights on when room or covered area is occupied and off when unoccupied, unless otherwise indicated.

1. Time Delay for Turning Lights Off:  Adjustable over a range from 1 to 15 minutes, minimum.

Subparagraph below specifies optional feature, available on some models.  Consult manufacturer's literature.

2. Ambient-Light-Level Control:  Adjustable for setting a level of ambient illumination above which sensor will not turn lights on when occupancy is sensed.

Select from three paragraphs below specifying examples of different sensor types.  Edit sensitivity requirements and other features to suit individual applications, or define in a schedule.  Coordinate with Drawings.

D. Passive-Infrared Type:  Detects occupancy by a combination of heat and movement in zone of coverage.  Each sensor detects occupancy anywhere in an area of 1000 sq. ft. (93 sq. m) by detecting occurrence of 6-inch (150-mm) minimum movement of any portion of a human body that presents a minimum target of 36 sq. in. (232 sq. cm) to the sensor.

E. Ultrasonic Type:  Emits a beam of ultrasonic energy and detects occupancy through use of Doppler's principle in discerning movement in zone of coverage by sensing a change in pattern of reflected ultrasonic energy.

F. Dual-Technology Type:  Uses a combination of passive-infrared and ultrasonic detection methods to distinguish between occupied and unoccupied conditions for area covered.  Particular technology or combination of technologies that controls each function (on or off) is selectable in the field by operating controls on unit.

2.6 MULTIPOLE CONTACTORS AND RELAYS

A. Description:  Electrically operated and mechanically held, and complying with UL 508 and NEMA ICS 2.

Edit two subparagraphs below for specific ratings if required.  Coordinate with Drawings.

1. Listed Current Rating for Switching: Consistent with type of load served, including tungsten filament, inductive, and high-inrush ballast (ballasts with 15 percent or less total harmonic distortion of normal load current).

2. Control Coil Voltage:  Match control power source.

PART 3 -  EXECUTION

3.1 INSTALLATION

Coordinate this Article with Drawings.

A. Mounting heights indicated are to bottom of unit for suspended devices and to center of unit for wall-mounting devices.

3.2 CONTROL WIRING INSTALLATION

Edit first paragraph below if wiring methods for lighting control are specified in a different Section from that referenced.

A. Install wiring between sensing and control devices according to manufacturer's written instructions and as specified in Division 16 Section "Basic Electrical Materials and Methods."

B. Bundle, train, and support wiring in enclosures.

3.3 IDENTIFICATION

A. Identify components and power and control wiring according to Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]."

3.4 FIELD QUALITY CONTROL

Delete nonapplicable items in first paragraph below.

A. Inspect control components for defects and physical damage, testing laboratory labeling, and nameplate compliance with the Contract Documents.

B. Electrical Tests:  Use particular caution when testing devices containing solid-state components.  Perform the following according to manufacturer's written instructions:

1. Continuity tests of circuits.

2. Operational Tests:  Set and operate devices to demonstrate their functions and capabilities in a methodical sequence that cues and reproduces actual operating functions. Record control settings, operations, and functional observations.

3. Correct deficiencies, make necessary adjustments, and retest.  Verify that specified requirements are met.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain lighting control devices.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 16145

LIGHTING CONTROL DEVICES
16145 - 1

