Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16215 - ELECTRICAL POWER MONITORING AND CONTROL

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes [monitoring] [monitoring and control] of electrical power and lighting circuits through electronic communication links between devices in distribution system components and power monitoring and control units.

1. Distribution system components, as referenced above, include the following:

Delete subparagraphs below for components not to be monitored or controlled.  Edit those retained to use nomenclature consistent with that used in other Sections of Project Specifications.

a. Medium-voltage switchgear.

b. Network protectors.

c. Transformers.

d. Low-voltage switchgear.

e. Switchboards.

f. Panelboards.

g. Motor controllers.

h. Motor-control centers.

i. Generator sets.

j. Transfer switches.

2. Power monitoring and control units include the following:

a. Local display panels.

b. Central-processing workstation personal computers.

c. Remote workstation personal computers.

1.2 DEFINITIONS

Retain special terms that remain after this Section has been edited.

A. Monitoring:  Acquisition, processing, communication, and display of equipment status data, metered electrical parameter values, event and alarm signals, tabulated reports, and event logs.

1.3 SUBMITTALS

A. Product Data:  List of components for power monitoring and control, including dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes.  Attach copies of Submittals for electrical distribution system components (such as switchboards and switchgear) that describe power monitoring and control features to coordinate Product Data related to power monitoring and control.

B. Shop Drawings:  Detail assemblies of standard components, custom assembled for specific application on this Project.

1. Outline Drawings:  Indicate dimensions, weights, arrangement of components, and clearance and access requirements.

2. Block Diagram:  Show interconnections between components specified in this Section and devices furnished with power distribution system components.  Indicate data communication paths and identify networks, data buses, data gateways, concentrators, and other devices to be used.  Describe characteristics of network and other data communication lines.

3. Wiring Diagrams:  Power, signal, and control wiring.

C. Software and Firmware Operational Documentation:  Include the following:

1. Software operating and upgrade manuals.

2. Program Software Backup:  On magnetic media or compact disc, complete with data files.

3. Device address list.

4. Printout of software application and graphic screens.

D. Software Upgrade Kit:  For Owner to use in modifying software to suit future power system revisions or power monitoring and control revisions.

E. Qualification data.

F. Field quality-control test reports.

G. Operation and maintenance data.

1.4 QUALITY ASSURANCE

A. Startup Personnel Qualifications:  Engage specially trained personnel who are directly employed by a manufacturer of distribution system protective devices.

B. Installer Qualifications:  A qualified installer, approved by manufacturer to install manufacturer's products.

C. Source Limitations:  Obtain power monitoring and control software, firmware, monitoring panels, and network components from the same manufacturer who is the source of distribution equipment circuit breakers and other protective devices.  This manufacturer's responsibilities include the following:

1. Ensuring compatibility of power monitoring and control features of electrical distribution components, including those provided in other Sections of these Specifications.

2. Integrating interconnected equipment and its communication functions and providing software and hardware interface components required for indicated functional operation.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E. Comply with 47 CFR 15, Subparts A and B, for Class A digital devices.

F. Comply with UL 916.

1.5 COORDINATION

A. Coordinate features of distribution equipment and power monitoring and control components to form an integrated interconnection of compatible components.

1. Match components and interconnections for optimum performance of specified functions.

B. Coordinate Work of this Section with that in Sections specifying distribution components that are monitored or controlled by power monitoring and control equipment.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. ABB Power T&D Company Inc.; Distribution Systems Division.

2. Cutler-Hammer Products; Eaton Corporation.

3. GE Electrical Distribution and Control.

4. Siemens Energy & Automation, Inc.

5. Square D Co.; Power Management Organization.

6. <Insert manufacturer.>

2.2 WORKSTATIONS AND SOFTWARE

A. Central-Processing Workstation:  Desktop PC installation capable of communicating with a minimum of [200] <Insert number> devices, and including the following minimum peripherals, accessories, and features:

1. RAM:  [32] <Insert number> MB.

2. Hard-Disk Drive:  [3] <Insert number> GB.

3. CPU:  [300] <Insert number> MHZ.

4. CD-ROM Drive:  [24] <Insert number>  X.

5. Floppy Disk Drive:  One.

6. Internal Zip Drive:  [100] <Insert number> MB.

7. Monitor:  [17 inch (532 mm)] <Insert size>.  Multisync with 0.25-mm mask pitch and [1024 by 768] <Insert number> resolutions at [100] <Insert number> Hz.

8. Operating System:  [Windows NT] [or] [Windows 95] <Insert system>.

9. Keyboard:  [Windows 95] <Insert system>.

10. One serial and one parallel port in addition to those required for power monitoring and control.

11. Network Interface Card:  Computer operated, with two-way communication transmitter-receiver chip.

12. Modem:  External, [56] <Insert speed>  K, minimum.

13. Automatic Reboot Capability:  When power is restored after an outage.

14. Printer:  Laser jet.  [Six] <Insert number> pages per minute minimum nominal printing rate in draft mode.

15. Backup Battery-Inverter Power Supply:  Automatic, rated [650] <Insert number>-VA output for 10 minutes.  Arranged to supply computer, accessories, and peripherals, not including a printer.  Include transient voltage surge suppressor and electromagnetic-interference filters.

B. Remote Workstations:  Desktop PCS that include the following features:

1. RAM:  [32] <Insert number> MB.

2. Hard-Disk Drive:  [3] <Insert number> GB.

3. CPU:  [300] <Insert number> MHZ.

4. CD-ROM Drive:  [24] <Insert number>  X.

5. Floppy Disk Drive:  One.

6. Monitor:  [15 inch (380 mm)] <Insert size>.  Multisync with [0.8] <Insert number>-mm dot pitch and [1024 by 768] <Insert number> resolutions at [100] <Insert number> Hz.

7. Operating System:  [Windows NT] [or] [Windows 95] <Insert system>.

8. Keyboard:  [Windows 95] <Insert system>.

9. One serial and one parallel port.

Delete first subparagraph below if access to network is by modem.

10. Network Interface Card:  Computer operated, with two-way communication transmitter-receiver chip.

11. Modem:  External, [56] <Insert speed>  K, minimum.

12. Automatic Reboot Capability:  When power is restored after an outage.

13. Printer:  Ink jet.  [Four] <Insert number> pages per minute minimum nominal printing rate in draft mode.

Delete items in first paragraph and subparagraphs below if not required for Project.

C. Metering and Monitoring Software:  Features and functions include the following:

1. Password Protection:  [Three] <Insert number> configurable security levels, minimum.

2. Operates in multitasking, multiuser environment.  [Windows NT] [or] [Windows 95] <Insert system> compliant.

3. On-Line Help:  Context sensitive.

4. Coordinates the communications of the network.

5. Provides interactive color-graphics platform with mouse-accessed menu and mouse-driven generation of distribution system graphics, including [site plan] [floor plans] [equipment elevations] [single-line diagram].

6. Provides mouse-driven interface with devices depicted in [single-line diagram] [and] [equipment elevation] screens.

7. Logs user-defined power monitoring and control and power distribution system events including log on/off; attempted log on/off; alarms; equipment operations; and out-of-limit, pickup, trip, and no-response events; with date and time stamps accurate to 0.1 second.

8. Exports and imports data to and from commonly used [Windows 95] <Insert system> spreadsheet, database, tenant billing, and other applications; uses dynamic data exchange technology.

9. Reports Trends:  Instantaneously, in a real-time or historical tabular format, bar chart, or user-defined time, trend plots of monitored parameters; unlimited as to interval, duration, or quantity of trends.

10. Manages Alarm Function:  Annunciates and logs alarm messages from discrete input and controls outputs, according to programmable security access protocol using the communication network.

a. Functions Requiring User Acknowledgment:  Run in background during computer use for other applications and override other presentations when they occur.

11. Defines and initiates load-shedding schemes responding to programmable time schedules, or set points of metered demands, or combinations of both.

D. Communication Software:  As recommended by manufacturer for high-speed communication via modem.

2.3 LOCAL DISPLAY PANEL

Coordinate this Article with Drawings.

A. Description:  Microprocessor-based, self-contained device mounted in a door of switchboard or switchgear and arranged to display values of parameters metered at each of the monitored circuit breakers in the host equipment.  Features include the following:

1. Communicates over power monitoring and control network.

2. Circuit breakers are selected for status and parameter display by programmable designations.

3. Circuit-breaker status and trip rating are displayed in addition to parameter values.

4. Nonvolatile memory retains programmed input data indefinitely during power outages.

5. Display Screen:  Light-emitting diode or illuminated liquid-crystal display, or approved equivalent.

2.4 COMMUNICATION COMPONENTS AND NETWORKS

A. Transient Voltage Surge Suppression and Electromagnetic-Interference Immunity:  Include in solid-state equipment.  Comply with IEEE C37.90.

B. Network Configuration:  High speed, multiaccess, open nonproprietary, industry standard communication protocol; LANs complying with EIA 485, IEEE 802.3, Ethernet, or other approved industry standard.

Below specifies low-speed network communications adequate for most monitoring and electrical alarm reporting and for simple control strategies.  Edit to require high-speed communications if equipment is to provide high-speed response for critical power system control functions.

C. Network Interface Modules:  Provide polling time supporting 30-second maximum interval between alarm initiation from monitored devices and registration and printout of alarm messages.

2.5 COMMUNICATION FEATURES OF POWER DISTRIBUTION SYSTEM DEVICES

Edit this Article to coordinate with Drawings and with Sections specifying distribution system components to be monitored or controlled.  Lack of coordination may result in monitoring functions inconsistent with equipment intended to provide them.  Specify basic features of components and their devices in those Sections and monitoring, control, and communication features in this Section.  For most components, use schedules (usually on Drawings) to indicate which devices are to be monitored or controlled and to define data to be monitored and type of control for each device.  See Evaluations.

A. Communication Function:  Microprocessor based and integral to devices indicated as having power monitoring or control functions.

1. Communication Address:  Unique to each individual device, and changeable at device.

2. Communication Protocol:  Match that of network to which connected.

3. Two-Way Communication:  Send and receive values, data, and control commands indicated.  Initiate alarm on malfunction of monitored device or monitoring equipment or network.

B. Circuit Breakers, 600 V and Less:  Include communication capability as a feature of the trip unit.

C. Medium-Voltage Circuit Breakers:  Include communication capability as a feature of the overcurrent relay trip unit.

D. Motor Controllers, 600 V and Less:  Include communication capability as a feature of the motor protection relay, or in a network interface card installed at the controller.

E. Multifunction Digital Meter:  Microprocessor-based device, flush or semiflush mounted in the door of switchboard or switchgear.  Unit shall display and communicate indicated monitoring parameters and data for circuit and inputs to which connected.  Unit shall have the ability to communicate as specified in "Communication Function" Paragraph above plus the following:

1. Status of up to three external contact-monitored alarm conditions monitored by internal meter relay functions.

2. Monitoring of a minimum of three programmable threshold values of metered parameters.

Items in two paragraphs and associated subparagraphs below are available from some manufacturers with both functions combined in a single device.

F. Addressable Monitoring Relay:  Continuously polled for data, via the communication network, as to the state (open or closed) of dry contacts of a contact-making sensing device.

1. Ability to Communicate:  As specified in "Communication Function" Paragraph above.

2. Power Supply Rating:  120-V ac or 48- to 125-V dc.

3. Enclosure:  NEMA 250, Type 12, unless otherwise indicated.

G. Addressable Control Relay:  Capable of being controlled from central-processing workstation to operate from C-dry contacts to provide on/off control of an independent circuit or device.

1. Ability to Communicate:  As specified in "Communication Function" Paragraph above.

2. Monitors status, on/off status of controlled contacts.

3. Power Supply Rating:  120-V ac or 48- to 125-V dc.

4. Enclosure:  NEMA 250, Type 12, unless otherwise indicated.

5. Contact Ratings:  Make 40 A, minimum; break 7 A, minimum.

2.6 ADDITIONAL POWER MONITORING AND CONTROL COMPONENTS

A. Current Transformers:  For multifunction digital meter and other current-monitoring equipment furnished under this Section that do not have integral current transformers, provide factory-mounted current-transformer units.

1. Primary Rating:  Equal to or more than that of associated circuit-breaker trip rating.  Equip with shorting switches.

B. Potential Transformers:  If those required for indicated monitoring functions are not integral to basic switchgear, circuit breakers, or circuit-breaker trip units, provide factory-mounted units.

1. Rating:  Same as distribution system phase-to-neutral voltage.

2. Protection:  Current-limiting fuses.

2.7 LOW-VOLTAGE WIRING

A. Data Line Cable:  Shielded, twisted-pair cable or other media recommended by manufacturer and as specified in Division 16 Section "Communication and Data-Processing Equipment."

B. Low-Voltage Control Cable:  Multiple conductor, color-coded, No. 20 AWG copper, minimum.

1. Conductor Insulation and Sheath:  PVC; except in plenum-type spaces, use sheathed cable listed for plenums.

2. Ordinary Switching Circuits:  Three conductors, unless otherwise indicated.

3. Switching Circuits with Pilot Lights or Locator Feature:  Five conductors, unless otherwise indicated.

2.8 ACCESSORIES

A. Interfaces with Distribution Equipment Specified in Other Sections:  Accessories, adapters, electronic interface units, and connections required for functional performance indicated.

PART 3 -  EXECUTION

3.1 INSTALLATION

Coordinate this Article with Drawings.

A. Install equipment level and plumb.  Anchor to building structural elements and support according to requirements in Division 16 Section "Basic Electrical Materials and Methods."

B. Mounting heights indicated are to bottom of unit for suspended items and to center of unit for wall-mounting items.

3.2 WIRING INSTALLATION

A. Install wiring between control devices as specified in Division 16 Section "[Conductors and Cables] [Basic Electrical Materials and Methods]" for low-voltage analog connections and in Division 16 Section "Communication and Data-Processing Equipment" for network and data line circuits.

Retain and edit first paragraph below or specify an alternate wiring method, such as cable tray.

B. Wiring Method:  Install wiring in raceway as specified in Division 16 Section "[Raceways and Boxes] [Basic Electrical Materials and Methods]" [unless run in accessible ceiling space or gypsum board partitions, where cable wiring may be used].

C. Bundle, train, and support wiring in enclosures.

3.3 IDENTIFICATION

A. Identify components and power and control wiring according to Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]."

B. Label each power monitoring and control module with a unique designation.

3.4 FIELD QUALITY CONTROL

A. Manufacturer's Field Services:  Engage a factory-authorized service representative to inspect field-assembled components and connections, to supervise pretesting, and adjustment of the system and to assist in final tests and demonstration.

B. Schedule visual and mechanical inspections and electrical tests with at least seven days' advance notice.

Delete inapplicable items below.

C. Inspect power monitoring and control components for defects and physical damage, labeling of testing laboratory, and nameplate compliance with the Contract Documents.

D. Electrical Tests:  Use particular caution when testing devices containing solid-state components.  Perform the following according to manufacturer's written instructions:

1. Continuity tests of circuits.

2. Operational Tests:  Set and operate controls at PC workstations and at monitored and controlled devices to demonstrate their functions and capabilities.  Use a methodical sequence that cues and reproduces actual operating functions as recommended by the manufacturer.  Note response to each test command and operation.  Note time intervals between initiation of alarm conditions and registration of alarms at central-processing workstation.

a. Coordinate testing required by this Section with that required by Sections specifying equipment being monitored and controlled.

b. Metering Test:  Load feeders, measure loads on feeder conductor with an RMS reading clamp-on ammeter, and simultaneously read indicated current on the same phase at the central-processing workstation.  Record and compare values measured at the two locations.  Resolve discrepancies greater than 10 percent and record resolution method and results.

E. Correct deficiencies, make necessary adjustments, and retest.  Verify that specified requirements are met.

F. Test Labeling:  After satisfactory completion of tests and inspections, apply a label to tested components indicating test results, date, and responsible agency and representative.

G. Reports:  Written reports of tests and observations.  Record defective materials and workmanship and unsatisfactory test results.  Record repairs and adjustments.

3.5 DEMONSTRATION

Services specified in this Article are optional; retain if Project warrants.  Revise hours below to suit Project.  Three or more sessions, three or more hours each, on different days may be required.  Coordinate with Division 1 training requirements.

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain electrical power monitoring and control.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

3.6 TELEPHONE TECHNICAL SUPPORT

A. Hardware and Software:  Within two years of date of Substantial Completion, provide unlimited response to user questions regarding software use and hardware and communication link troubleshooting, reconfiguring, and adjusting.

1. Telephone Calls:  Toll free.

2. Availability:  Eight hours per day, weekdays.

3. Responder Qualifications:  Engineer or technician thoroughly familiar with power monitoring and control equipment.

END OF SECTION 16215

ELECTRICAL POWER MONITORING AND CONTROL
16215 - 1

