Copyright 1997 AIA
MASTERSPEC
3/97


Copyright 1997, The American Institute of Architects (AIA)

SECTION 16231 - PACKAGED ENGINE GENERATORS

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged diesel-engine generator sets with the following features and accessories:

Edit list below to suit Project.

1. Battery charger.

2. Day tank.

3. Engine generator set.

4. Muffler.

5. Exhaust piping external to set.

6. Outdoor enclosure.

7. Remote annunciator.

8. Remote radiator.

9. Remote stop switch.

10. Starting battery.

11. Load bank.

12. Load-bank remote-control panel.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 15 Section "Mechanical Vibration Controls and Seismic Restraints" for muffler and exhaust piping supports.

2. Division 15 Section "Pipe Insulation" for muffler and exhaust pipe insulation.

3. Division 15 Section "Fuel Oil Piping" for interior fuel piping and fuel storage tank.

4. Division 15 Section "Hydronic Piping" for coolant piping external to engine generator.

5. Division 15 Section "Metal Ducts" for combustion air and radiator fan discharge connections.

6. Division 16 Section "Transfer Switches" for transfer switches, including sensors and relays to initiate automatic-starting and -stopping signals for engine generator sets.

1.3 DEFINITIONS

A. Standby Rating:  Power output rating equal to the power the generator set delivers continuously under normally varying load factors for the duration of a power outage.

B. Operational Bandwidth:  The total variation from the lowest to highest value of a parameter over the range of conditions indicated, expressed as a percentage of the nominal value of the parameter.

C. Steady-State Voltage Modulation:  The uniform cyclical variation of voltage within the operational bandwidth, expressed in Hertz or cycles per second.

1.4 SUBMITTALS

A. Product Data:  Include data on features, components, ratings, and performance.  Include the following:

1. Dimensioned outline plan and elevation drawings of engine generator set and other components specified.

2. Thermal damage curve for generator.

3. Time-current characteristic curves for generator protective device.

B. Shop Drawings:  Indicate fabrication details, dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Design Calculations:  Signed and sealed by a qualified professional engineer.  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

2. Vibration Isolation Base Details:  Signed and sealed by a qualified professional engineer.  Detail fabrication, including anchorages and attachments to structure and to supported equipment.  Include base weights.

3. Wiring Diagrams:  Detail wiring for power and control connections and differentiate between factory-installed and field-installed wiring.

C. Qualification Data:  For firms and persons specified in "Quality Assurance" Article.

D. Field Test and Observation Reports:  Indicate and interpret test results and inspection records relative to compliance with performance requirements.

Delete paragraph below if not required.  See Editing Instruction No. 2 in the Evaluations.

E. Certified summary of prototype-unit test report.

F. Certified Test Reports:  For components and accessories that are equivalent, but not identical, to those tested on prototype unit.

Include paragraph below for generator sets specified to meet performance requirements and for generator sets serving sensitive loads.

G. Certified Summary of Performance Tests:  Demonstrate compliance with specified requirement to meet performance criteria for sensitive loads.

H. Factory Test Reports:  For units to be shipped for this Project, showing evidence of compliance with specified requirements.

Normally delete paragraph below.  See Evaluations.

I. Exhaust Emissions Test Report:  To show compliance with applicable regulations.

J. Sound or noise measurement test report.

K. Certification of Torsional Vibration Compatibility:  Comply with NFPA 110.

L. Field test report of tests specified in Part 3.

M. Maintenance Data:  For each packaged engine generator and accessories to include in maintenance manuals specified in Division 1.  Include the following:

Delete subparagraph below except for remote locations.

1. List of tools and replacement items recommended to be stored at the Project for ready access.  Include part and drawing numbers, current unit prices, and source of supply.

2. Detail operating instructions for both normal and abnormal conditions.

1.5 QUALITY ASSURANCE

Revise response time in paragraph below to suit Project.

A. Manufacturer Qualifications:  Maintain a service center capable of emergency maintenance and repairs at the Project with eight hours' maximum response time.

Delete paragraph below except for projects where Contractor selects independent testing agency.  Coordinate with corresponding requirements for automatic transfer switches.

B. Testing Agency Qualifications:  Testing agency as defined by OSHA in 29 CFR 1910.7 or a member company of the InterNational Electrical Testing Association and that is acceptable to authorities having jurisdiction.

C. Source Limitations:  Obtain packaged engine generator and auxiliary components specified in this Section through one source from a single manufacturer.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction.

E. Comply with NFPA 70.

Delete paragraph below except for healthcare facilities.

F. Comply with NFPA 99.

G. Comply with NFPA 110 requirements for Level 1 emergency power supply system.

Select paragraph above or below if generator set is automatically started.  Delete both for manually started units.  See Editing Instruction No. 3 in the Evaluations.

H. Comply with NFPA 110 requirements for Level 2 emergency power supply system.

Delete below unless State or local compliance is required.  Edit to suit Project.

I. Engine Exhaust Emissions:  Comply with applicable state and local government requirements.

Delete below except for installations with critical noise abatement requirements, particularly outdoor generator sets.  Edit to suit local situation.  Coordinate with noise-reduction features included in the design, including those relating to cooling-air intake and discharge arrangement and muffler specification and its location and orientation as shown on Drawings.

J. Noise Emission:  Comply with [applicable state and local government requirements] <Insert other Project criteria> for maximum noise level at [adjacent property boundaries] <Insert other critical locations> due to sound emitted by generator set including engine, engine exhaust, engine cooling-air intake and discharge, and other components of the installation.

1.6 DELIVERY, STORAGE, AND HANDLING

A. Deliver engine generator set and system components to their final locations in protective wrappings, containers, and other protection that will exclude dirt and moisture and prevent damage from construction operations.  Remove protection only after equipment is safe from such hazards.

1.7 WARRANTY

Retain this Article if a special warranty is required for engine generator and auxiliary components.  See Evaluations.

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Warranties."

A. General Warranty:  Special warranty specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

B. Special Warranty:  Written warranty, executed by manufacturer agreeing to repair or replace packaged engine generator and auxiliary components that fail in materials or workmanship within specified warranty period.

Revise warranty to period required and verify availability.  Period below is maximum included with manufacturer's published data.

1. Warranty Period:  Five years from date of Substantial Completion.

1.8 MAINTENANCE SERVICE

Retain below for critical installations and consider including a provision for submitting a continuing maintenance Agreement proposal.  Revise starting date if required.  Obtain a copy of maintenance Agreement before retaining or editing below.  Maintenance contracts may not be allowed for publicly funded projects.

A. Maintenance:  At Substantial Completion, begin 12 months' full maintenance by skilled employees of the manufacturer's designated service organization.  Include quarterly exercising to check for proper, starting, load transfer, and running under load.  Include routine preventive maintenance as recommended by manufacturer and adjusting as required for proper operation.  Maintenance agreements shall include parts and supplies as used in the manufacture and installation of original equipment.

1.9 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Quantities below are examples only.  Revise to suit Project.

1. Fuses:  One for every ten of each type and rating, but not less than one of each.

2. Indicator Lamps:  Two for every six of each type used, but not less than two of each.

3. Filters:  One set each of lubricating oil, fuel, and combustion-air filters.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1. Caterpillar, Inc.; Engine Div.

2. Generac Corp.

3. Kohler Co; Generator Division.

4. MagneTek, Inc.

5. Onan Corp; Industrial Business Group.

6. Penn Detroit Allison.

7. Spectrum Detroit Diesel.

8. Stewart & Stevenson Services, Inc.

9. Western Diesel Services.

2.2 ENGINE GENERATOR SET

A. Furnish a coordinated assembly of compatible components.

Delete one of two paragraphs below.

B. Output Connections:  Three phase, four wire.

C. Output Connections:  Three phase, three wire.

D. Safety Standard:  Comply with ASME B15.1.

E. Nameplates:  Each major system component is equipped with a conspicuous nameplate of component manufacturer.  Nameplate identifies manufacturer of origin and address, and model and serial number of item.

Delete below if Project is not located in seismic risk zone 3 or 4 of Uniform Building Code as modified by authorities having jurisdiction.  See Editing Instruction No. 5 in the Evaluations.

F. Resistance to Seismic Forces:  Supports for internal and external components, and fastenings for batteries, wiring, and piping are designed and constructed to withstand static or anticipated seismic forces, or both, in any direction.  For each item, use a minimum force value equal to weight of item.

Delete paragraph below if dimensions are not critical.  Coordinate with Drawings.

G. Limiting dimensions indicated for system components are not exceeded.

Coordinate paragraph below with prototype test requirements in "Submittals" and "Source Quality Control" articles.

H. Power Output Ratings:  Nominal ratings as indicated, with capacity as required to operate as a unit as evidenced by records of prototype testing.

I. Skid:  Adequate strength and rigidity to maintain alignment of mounted components without depending on a concrete foundation.  Skid is free from sharp edges and corners.  Lifting attachments are arranged to facilitate lifting with slings without damaging any components.

Delete below for units where rigging is not required.

J. Rigging Diagram:  Inscribed on a metal plate permanently attached to skid.  Diagram indicates location and lifting capacity of each lifting attachment and location of center of gravity.

Select one of two articles below to match overall generator-set performance to basic load characteristics of Project.  Edit performance to specific needs.

First Article is for loads involving little or no sensitive electronic equipment, adjustable frequency drives, or uninterruptible power supply systems.  See Evaluations.

2.3 GENERATOR-SET PERFORMANCE

A. Steady-State Voltage Operational Bandwidth:  4 percent of rated output voltage from no load to full load.

B. Steady-State Voltage Modulation Frequency:  Less than 1 Hz.

C. Transient Voltage Performance:  Not more than 20 percent variation for 50 percent step-load increase or decrease.  Voltage recovers to remain within the steady-state operating band within three seconds.

D. Steady-State Frequency Operational Bandwidth:  0.5 percent of rated frequency from no load to full load.

E. Steady-State Frequency Stability:  When system is operating at any constant load within rated load, there are no random speed variations outside the steady-state operational band and no hunting or surging of speed.

F. Transient Frequency Performance:  Less than 5 percent variation for a 50 percent step-load increase or decrease.  Frequency recovers to remain within the steady-state operating band within five seconds.

G. Output Waveform:  At no load, harmonic content measured line to line or line to neutral does not exceed 5 percent total and 3 percent for single harmonics.  The telephone influence factor, determined according to NEMA MG 1, shall not exceed 50.

H. Sustained Short-Circuit Current:  For a three-phase, bolted short circuit at system output terminals, the system will supply a minimum of 250 percent of rated full-load current for not less than 10 seconds and then clear the fault automatically, without damage to any generator system component.

Paragraph below requires 10-second maximum start time under specific conditions and includes startup only, not load assumption.  Retain, delete, or revise to suit Project.

I. Start Time:  Comply with NFPA 110, Type 10, system requirements.

Select Article below for loads involving sensitive electronic equipment, significant nonlinear load elements, or uninterruptible power supply systems.  Coordinate with "Governor" and "Generator, Exciter, and Voltage Regulator" articles.  See Evaluations.

2.4 GENERATOR-SET PERFORMANCE FOR SENSITIVE LOADS

A. Oversizing generator compared with the rated power output of the engine to meet performance requirements in paragraphs below is permissible.

1. Nameplate Data for Oversized Generator:  Show ratings required by the Contract Documents rather than ratings that would normally be applied to generator size installed.

B. Steady-State Voltage Operational Bandwidth:  2 percent of rated output voltage from no load to full load.

C. Steady-State Voltage Modulation Frequency:  Less than 1 Hz.

D. Transient Voltage Performance:  Not more than 10 percent variation for 50 percent step-load increase or decrease.  Voltage recovers to remain within the steady-state operating band within 0.5 second.

E. Steady-State Frequency Operational Bandwidth:  Plus or minus 0.25 percent of rated frequency from no load to full load.

F. Steady-State Frequency Stability:  When system is operating at any constant load within the rated load, there are no random speed variations outside the steady-state operational band and no hunting or surging of speed.

G. Transient Frequency Performance:  Less than 2-Hz variation for a 50 percent step-load increase or decrease.  Frequency recovers to remain within the steady-state operating band within three seconds.

H. Output Waveform:  At no load, harmonic content measured line to neutral does not exceed 2 percent total with no slot ripple.  The telephone influence factor, determined according to NEMA MG 1, shall not exceed 50.

I. Sustained Short-Circuit Current:  For a three-phase, bolted short circuit at system output terminals, the system will supply a minimum of 300 percent of rated full-load current for not less than 10 seconds and then clear the fault automatically, without damage to winding insulation or any other generator system component.

J. Excitation System:  Performance is unaffected by voltage distortion caused by nonlinear load.

Below requires 10-second maximum start time under specific conditions and includes startup only, not load assumption.  Retain, delete, or revise to suit Project.

K. Start Time:  Comply with NFPA 110, Type 10, system requirements.

2.5 SERVICE CONDITIONS

A. Environmental Conditions:  Engine generator system withstands the following environmental conditions without mechanical or electrical damage or degradation of performance capability:

Select one of two ambient temperatures below.  Select first subparagraph if generator-set start time must be within NFPA 110 limits.  (This usually implies installation indoors in heated space).  Coordinate with Drawings.

1. Ambient Temperature:  5 to 40 deg C.

2. Ambient Temperature:  Minus 15 to plus 40 deg C.

Delete subparagraph below for outdoor units.

3. Relative Humidity:  0 to 95 percent.

Revise altitude below to actual altitude of installation.

4. Altitude:  Sea level to 1000 feet (300 m).

If unusual service conditions for equipment exist and cannot be eliminated, specify them in paragraph below.  See Editing Instruction No. 4 in the Evaluations.

B. Unusual Service Conditions:  Engine generator equipment and installation are required to operate under the following conditions:

Below is an example only.  Revise to list unusual conditions.

1. High salt-dust content in the air due to sea-spray evaporation.

2.6 ENGINE

A. Comply with NFPA 37.

Revise fuel grade in paragraph below to suit local use.

B. Fuel:  Fuel oil, Grade DF-2.

C. Rated Engine Speed:  1800 rpm.

D. Maximum Piston Speed for Two-Cycle Engines:  1725 fpm (8.8 m/s).

E. Maximum Piston Speed for Four-Cycle Engines:  2250 fpm (11.4 m/s).

F. Lubrication System:  Pressurized by a positive-displacement pump driven from engine crankshaft.  The following items are mounted on engine or skid:

1. Filter and Strainer:  Rated to remove 90 percent of particles 5 micrometers and smaller while passing full flow.

2. Thermostatic Control Valve:  Controls flow in system to maintain optimum oil temperature.  Unit is capable of full flow and is designed to be fail-safe.

3. Crankcase Drain:  Arranged for complete gravity drainage to an easily removable container with no disassembly and without use of pumps or siphons or special tools or appliances.

G. Engine Fuel System:  Comply with NFPA 37.  System includes the following:

1. Main Fuel Pump:  Mounted on engine.  Pump ensures adequate primary fuel flow under starting and load conditions.

2. Relief/Bypass Valve:  Automatically regulates pressure in fuel line and returns excess fuel to source.

Delete paragraph below if not required.  NFPA 110 contains temperature requirements.  Coordinate with Drawings for electrical supply.

H. Coolant Jacket Heater:  Electric-immersion type, factory installed in coolant jacket system.  Comply with NFPA 110 requirements for Level 1 equipment.

2.7 GOVERNOR

Select one governor type below consistent with steady-state and transient frequency tolerances of loads supplied.  Coordinate with performance Article selected above.  Retain first type for systems with sensitive loads.

A. Type:  Adjustable isochronous, with speed sensing.

B. Type:  Mechanical.

2.8 ENGINE COOLING SYSTEM

Select one of two paragraphs below or edit to describe other cooling-system arrangements.  Coordinate with Drawings.  See Editing Instruction No. 6 in the Evaluations.

A. Description:  Closed loop, liquid cooled, with radiator factory mounted on engine generator-set skid and integral engine-driven coolant pump.

B. Description:  Closed loop, liquid cooled, with remote radiator and integral engine-driven coolant pump.

Select one of three paragraphs below for radiator consistent with paragraph selected above.  Coordinate with Drawings.

C. Radiator:  Rated for specified coolant.

D. Remote Radiator:  Vertical air discharge.  Unit is rated for specified coolant.

E. Remote Radiator:  Horizontal air discharge.  Unit is rated for specified coolant.

Modify subparagraph below if aluminum core is permissible.

1. Radiator Core Tubes:  Nonferrous-metal construction other than aluminum.

Delete subparagraph below if separate expansion tank is in design.

2. Size of Radiator:  Adequate to contain expansion of total system coolant from cold start to 110 percent load condition.

Select one of two subparagraphs below.

3. Fan:  Driven by multiple belts from engine shaft.

4. Fan:  Driven by totally enclosed electric motor with sealed bearings.

F. Coolant:  Solution of 50 percent ethylene-glycol-based antifreeze and 50 percent water, with anticorrosion additives as recommended by engine manufacturer.

Delete paragraph below unless containment of coolant expansion by radiator is marginal or inadequate.  Coordinate with Drawings.

G. Expansion Tank:  Constructed of welded steel plate and equipped with gage glass and petcock.

H. Temperature Control:  Self-contained, thermostatic-control valve modulates coolant flow automatically to maintain optimum constant coolant temperature as recommended by engine manufacturer.

I. Coolant Hose:  Flexible assembly with inside surface of nonporous rubber and outer covering of aging-, ultraviolet-, and abrasion-resistant fabric.

1. Rating:  50-psig (345-kPa) maximum working pressure with 180 deg F (82 deg C) coolant, and noncollapsible under vacuum.

2. End Fittings:  Flanges or steel pipe nipples with clamps to suit piping and equipment connections.

Delete below for generator sets with integrally mounted radiators or if shown on mechanical Drawings and specified in Division 15 Sections.

J. Coolant piping external to engine generator set.  Use ASTM B 88, Type L (ASTM B 88M, Type B) copper tubing with brazed joints, sized as recommended by diesel engine manufacturer.  Refer to Division 15 Section "Basic Mechanical Materials and Methods" for basic piping installation and joint construction.  Refer to Division 15 Section "Hydronic Piping" for materials and installation requirements for piping.

2.9 FUEL SUPPLY SYSTEM

A. Comply with NFPA 30 and NFPA 37.

Fuel tanks mounted within generator-set base are available as well as freestanding day- tank units specified below.

B. Day Tank:  Freestanding, factory-fabricated assembly of a fuel tank listed by a nationally recognized testing laboratory, with integral, float-controlled transfer pump and the following features:

1. Containment:  Integral rupture basin with a capacity of 150 percent of nominal capacity of day tank.

a. Leak Detector:  Locate in rupture basin and connect to provide audible and visual alarm in the event of day-tank leak.

Revise hours in subparagraph below to suit Project or delete subparagraph and indicate capacity on Drawings.  Coordinate with Drawings and NFPA 110 requirements.

2. Tank Capacity:  Adequate to supply fuel to engine for an uninterrupted period of four hours' operation at 100 percent of rated power output of engine generator system without being refilled.

3. Pump Capacity:  Exceeds maximum flow of fuel drawn by engine-mounted fuel supply pump at 110 percent of rated capacity, including fuel returned from engine.

4. Unit, Including Alarm Contacts:  Complies with UL 142.

5. Low-Level Alarm Sensor:  Separate device operates alarm contacts at 75 percent of normal fuel level.

Edit subparagraph below to suit Project or delete if not required.  Coordinate with "Control and Monitoring" Article.

6. High-Level Alarm Sensor:  Separate device operates alarm and redundant fuel shutoff contacts at 106 percent of normal fuel level.

7. Piping Connections:  Include fuel suction and return lines to fuel storage tank; fuel supply; and return lines to engine, local fuel fill, vent line, overflow line, and tank drain line complete with shutoff valve.

Subparagraph below is not in NFPA 110 minimum requirements.  Retain, delete, or revise to suit Project.

8. Redundant High-Level Fuel Shutoff:  Actuated by high-level alarm sensor in day tank.  It operates a separate motor device that disconnects day-tank pump motor.  It also closes a solenoid valve in fuel suction line from fuel storage tank to day tank.  Both items remain in shutoff state until manually reset.  Shutoff action initiates an alarm signal to control panel but does not shut down engine generator set.

C. Base-Mounted Fuel Oil Tank:  Factory-installed and -piped, listed and labeled fuel oil tank.  Features include the following:

1. Tank level indicator.

Revise capacity below to suit Project.  Consult manufacturers regarding capacities available for size of set used on Project.

2. Capacity:  Fuel for eight hours' continuous operation at 100 percent rated power output.

3. Vandal-resistant fill cap.

Determine applicable codes and regulations, and coordinate subparagraph below with Drawings.

4. Containment Provisions:  Comply with requirements of authorities having jurisdiction.

D. Fuel Oil Piping and Remote Fuel Oil Storage Tank:  As specified in Division 2 Section "Fuel-Oil Distribution."

E. Interior Fuel Oil Piping:  As specified in Division 15 Section "Fuel Oil Piping."

2.10 ENGINE EXHAUST SYSTEM

Select one of three paragraphs below for muffler.

A. Muffler:  Critical type, sized as recommended by engine manufacturer.  Measured sound level at a distance of 10 feet (3 m) from exhaust discharge, is 85 dBA or less.

B. Muffler:  Residential type, sized as recommended by engine manufacturer.  Measured sound level at a distance of 10 feet (3 m) from exhaust discharge, is 95 dBA or less.

C. Muffler:  Industrial type, sized as recommended by engine manufacturer.  Measured sound level in the 20- to 75-Hz frequency band at a distance of 25 feet (8 m) from exhaust discharge, is 87 dBA or less.

Coordinate paragraphs below with Drawings.

D. Condensate Drain for Muffler:  Schedule 40, black steel pipe connected to muffler drain outlet through a petcock.

E. Connections from Engine to Exhaust System:  Flexible section of corrugated stainless-steel pipe.

F. Connection from Exhaust Pipe to Muffler:  Stainless-steel expansion joint with liners.

G. Insulation for Mufflers and Indoor Exhaust Piping:  As specified in Division 15 Section "Pipe Insulation."

H. Supports for Muffler and Exhaust Piping:  Spring hangers and all-thread rods and vibration hangers as specified in Division 15 Section "Mechanical Vibration Controls and Seismic Restraints"; attached to building structure.

I. Exhaust Piping External to Engine:  ASTM A 53, Schedule 40, welded, black steel, with welded joints and fittings.  Refer to Division 15 Section "Basic Mechanical Materials and Methods" for basic piping installation and joint construction.  Refer to Division 15 Section "Hydronic Piping" for materials and installation requirements for piping.

2.11 COMBUSTION-AIR-INTAKE

Select "heavy-duty" option below if filters may not be serviced as often as recommended.  If air contaminant level is excessive, consult manufacturers to determine if special filtration of combustion air is needed.

A. Description:  [Standard-duty] [Heavy-duty] engine-mounted air cleaner with replaceable dry filter element and "blocked filter" indicator.

2.12 STARTING SYSTEM

Select one of two paragraphs below.

A. Description:  12-V electric, with negative ground and including the following items:

B. Description:  24-V electric, with negative ground and including the following items:

1. Components:  Sized so they will not be damaged during a full engine-cranking cycle with ambient temperature at maximum specified in "Environmental Conditions" Paragraph in "Service Conditions" Article above.

2. Cranking Motor:  Heavy-duty unit that automatically engages and releases from engine flywheel without binding.

Select first subparagraph below if system description in Part 1 specifies a level 1 or level 2 system per NFPA 110.  Otherwise, select second subparagraph.  See Editing Instruction No. 7 in the Evaluations.

3. Cranking Cycle:  As required by NFPA 110 for system level specified.

4. Cranking Cycle:  60 seconds.

Select one of two subparagraphs below.  First complies with NFPA 110 requirements.  Second is a more conservative rule used for some industrial applications.

5. Battery:  Adequate capacity within ambient temperature range specified in "Environmental Conditions" Paragraph in "Service Conditions" Article above to provide specified cranking cycle at least twice without recharging.

6. Battery:  Adequate capacity within ambient temperature range specified in "Environmental Conditions" Paragraph in "Service Conditions" Article above to provide specified cranking cycle at least three times without recharging.

Coordinate subparagraph below with Drawings.

7. Battery Cable:  Size as recommended by generator set manufacturer for cable length indicated.  Include required interconnecting conductors and connection accessories.

Delete subparagraph below if compartment is not required or modify to suit Project.

8. Battery Compartment:  Factory fabricated of metal with acid-resistant finish and thermal insulation.  Thermostatically controlled heater is arranged to maintain battery above 10 deg C regardless of external ambient temperature within range specified in "Environmental Conditions" Paragraph in "Service Conditions" Article above.  Include accessories required to support and fasten batteries in place.

9. Battery-Charging Alternator:  Factory mounted on engine with solid-state voltage regulation and 35-A minimum continuous rating.

10. Battery Charger:  Current-limiting, automatic-equalizing and float-charging type.  Unit complies with UL 1236 and includes the following features:

a. Operation:  Equalizing-charging rate of 10 A is initiated automatically after battery has lost charge until an adjustable equalizing voltage is achieved at battery terminals.  Unit then automatically switches to a lower float-charging mode and continues operating in that mode until battery is discharged again.

b. Automatic Temperature Compensation:  Adjusts float and equalizes voltages for variations in ambient temperature from minus 40 deg C to plus 60 deg C to prevent overcharging at high temperatures and undercharging at low temperatures.

c. Automatic Voltage Regulation:  Maintains output voltage constant regardless of input voltage variations up to plus or minus 10 percent.

d. Ammeter and Voltmeter:  Flush mounted in door.  Meters indicate charging rates.

Subparagraph below covers sensing for safety indications on control and monitoring panel.  NFPA 110 requires sensing for level 1 systems and makes sensing optional for level 2 systems.  Edit to suit Project.  See Editing Instruction No. 3 in the Evaluations.

e. Safety Functions:  Include sensing of abnormally low battery voltage arranged to close contacts providing low battery voltage indication on control and monitoring panel.  Also include sensing of high battery voltage and loss of ac input or dc output of battery charger.  Either condition closes contacts that provide a battery-charger malfunction indication at system control and monitoring panel.

f. Enclosure and Mounting:  NEMA 250, Type 1, wall-mounted cabinet.

2.13 CONTROL AND MONITORING

This Article specifies the subsystem that monitors, protects, and controls the engine generator.  See Editing Instruction No. 8 in the Evaluations.

Select first paragraph below for automatically started systems, second paragraph for manually started systems.

A. Functional Description:  When the mode-selector switch on the control and monitoring panel is in the automatic position, remote-control contacts in one or more separate automatic-transfer switches initiate starting and stopping of the generator set.  When the mode-selector switch is switched to the on position, the generator set manually starts.  The off position of the same switch initiates generator-set shutdown.  When the generator set is running, specified system or equipment failures or derangements automatically shut down the generator set and initiate alarms.  Operation of a remote emergency-stop switch also shuts down the generator set.

B. Functional Description:  Switching on-off switch on the generator control panel to the on position starts the generator set.  The off position of the same switch initiates generator-set shutdown.  When the generator set is running, specified system or equipment failures or derangements automatically shut down the generator set and initiate alarms.  Operation of a remote emergency-stop switch also shuts down the generator set.

Select one of three paragraphs below to describe control and monitoring unit configuration.  Coordinate with Drawings.  Retain first paragraph, unless special requirements justify significant extra cost of one of the other two special arrangements.  See Evaluations.

C. Configuration:  Operating and safety indications, protective devices, basic system controls, and engine gages are grouped on a common control and monitoring panel mounted on the generator set.  Mounting method isolates the control panel from generator-set vibration.

D. Configuration:  Operating and safety indications, protective devices, basic system controls, and engine gages are grouped in a common wall-mounted control and monitoring panel.

E. Configuration:  Operating and safety indications, protective devices, basic system controls, engine gages, instrument transformers, generator disconnect switch or circuit breaker, and other indicated components are grouped in a combination control and power panel.  Control and monitoring section of panel is isolated from power sections by steel barriers.  Panel features include the following:

Select one of three subparagraphs below to further define control and power panel in last "configuration" paragraph above.

1. Wall-Mounted Cabinet Construction:  Rigid, self-supporting steel unit complying with NEMA ICS 6.  Power bus is copper.  Bus, bus supports, control wiring, and temperature rise comply with UL 891.

2. Switchboard Construction:  Unit is freestanding and complies with Division 16 Section "Switchboards."

3. Switchgear Construction:  Unit is freestanding and complies with Division 16 Section "Switchgear."

4. Current and Potential Transformers:  Instrument accuracy class.

Select one of three paragraphs below to specify minimum control and monitoring panel features.  First two are for standardized panels for automatically started units.  Third is for a typical manually operated generator system.  Coordinate with Drawings.  See Editing Instruction No. 9 in the Evaluations.

F. Indicating and Protective Devices and Controls:  Include those required by NFPA 110 for a Level 1 system, and the following:

G. Indicating and Protective Devices and Controls:  Include those required by NFPA 110 for a Level 2 system, and the following:

H. Indicating and Protective Devices and Controls:  Include the following:

Retain nine items below with any paragraph above.

1. AC voltmeter.

2. AC ammeter.

3. AC frequency meter.

4. DC voltmeter (alternator battery charging).

5. Engine-coolant temperature gage.

6. Engine lubricating-oil pressure gage.

7. Running-time meter.

8. Ammeter-voltmeter, phase-selector switch(es).

9. Generator-voltage adjusting rheostat.

Delete five devices below except for manually started units (not covered by NFPA 110).  Coordinate with Drawings.  See Evaluations for typical local and remote alarm indications and shutdowns.

10. Start-stop switch.

11. Overspeed shutdown device.

12. Coolant high-temperature shutdown device.

13. Coolant low-level shutdown device.

14. Oil low-pressure shutdown device.

Delete two subparagraphs below, unless required.

15. Fuel tank derangement alarm.

16. Fuel tank high-level shutdown of fuel supply alarm.

Include subparagraph below for units with "Generator Protector" feature.

17. Generator overload.

I. Supporting Items:  Include sensors, transducers, terminals, relays, and other devices, and wiring required to support specified items.  Locate sensors and other supporting items on engine, generator, or elsewhere as indicated.  Where not indicated, locate to suit manufacturer's standard.

Feature in paragraph below facilitates connection, under this or future Contract, to building automation or building control and monitoring system.  Coordinate with Drawings and Section covering data transmission and data terminals.

J. Connection to Data Link:  A separate terminal block, factory wired to Form C dry contacts, for each alarm and status indication is reserved for connections for data link transmission of indications to remote data terminals.  Data system connections to terminals are covered in another Section.

Delete one or both paragraphs below to suit Project or applicable codes and standards.  Evaluations discuss what will be obtained by selecting first paragraph.  Coordinate with Drawings.

K. Common Remote Audible Alarm:  Comply with NFPA 110 requirements for Level 1 systems.  Include necessary contacts and terminals in control and monitoring panel.  Locate audible device and silencing means where indicated.

Use paragraph below for manually started systems or for automatically started systems not specified to comply with NFPA 110, level 1, but where some remote alarm functions are needed.  Coordinate with Drawings.

L. Common Remote Audible Alarm:  Signal the occurrence of any events listed below without differentiating between event types.  Locate audible device and silencing means where indicated.  Connect so that after an alarm is silenced, clearing of initiating condition will reactivate alarm until silencing switch is reset.

Delete subparagraphs below if not required to initiate common remote audible alarm in paragraph above.  Do not list events if paragraph requiring compliance with NFPA 110 is used, since NFPA 110 specifically designates alarm events to be signaled.

1. Engine high-temperature shutdown.

2. Lube-oil low-pressure shutdown.

3. Overspeed shutdown.

4. Remote emergency-stop shutdown.

5. Engine high-temperature prealarm.

6. Lube-oil low-pressure prealarm.

7. Fuel tank low level.

Delete subparagraphs below for manually started systems.  For automatically started systems, continue list above with items selected below to suit Project.

8. Overcrank shutdown.

9. Coolant low-temperature alarm.

10. Control switch not in auto position.

11. Battery-charger malfunction alarm.

12. Battery low-voltage alarm.

Retain paragraph below for systems required to comply with NFPA 99 or where otherwise needed.  Modify if all indications required by NFPA 99 are not needed.  Coordinate with Drawings.

M. Remote Alarm Annunciator:  Comply with NFPA 99.  Labeled LEDs identify each alarm event.  Common audible signal sounds for alarm conditions.  Silencing switch in face of panel silences signal without altering visual indication.  Connect so that after an alarm is silenced, clearing of initiating condition will reactivate alarm until silencing switch is reset.  Cabinet and faceplate are surface- or flush-mounting type to suit mounting conditions indicated.

Coordinate below with Drawings.

N. Remote Emergency-Stop Switch:  Flush wall-mounted, unless otherwise indicated and prominently labeled.  Push button is protected from accidental operation.

2.14 GENERATOR OVERCURRENT AND FAULT PROTECTION

Select one or more items from six paragraphs below to specify disconnect switch(es) and protective devices for the generator (alternator) component of the generator set.  See Editing Instruction No. 10 in the Evaluations.

Select one of first four paragraphs below.  Retain first paragraph for units smaller than 200 kW where budget constraints are severe.  Device provides little or no generator protection and no selectivity with downstream circuit protective devices.

A. Generator Circuit Breaker:  Molded-case, thermal-magnetic type; 100 percent rated; complying with NEMA AB 1 and UL 489.

1. Tripping Characteristic:  Designed specifically for generator protection.

2. Trip Rating:  Matched to generator rating.

3. Shunt Trip:  Connected to trip breaker when generator set is shut down by other protective devices.

4. Mounting:  Adjacent to or integrated with control and monitoring panel.

B. Generator Circuit Breaker:  Molded-case, electronic-trip type; 100 percent rated; complying with UL 489.

1. Tripping Characteristics:  Adjustable long-time and short-time delay and instantaneous.

2. Trip Settings:  Matched to generator thermal damage curve as closely as possible.

3. Shunt Trip:  Connected to trip breaker when generator set is shut down by other protective devices.

4. Mounting:  Adjacent to or integrated with control and monitoring panel.

C. Generator Circuit Breaker:  Insulated-case, electronic-trip type; 100 percent rated; complying with UL 489.

1. Tripping Characteristics:  Adjustable long-time and short-time delay and instantaneous.

2. Trip Settings:  Matched to generator thermal damage curve as closely as possible.

3. Shunt Trip:  Connected to trip breaker when generator set is shut down by other protective devices.

4. Mounting:  Adjacent to or integrated with control and monitoring panel.

Delete three paragraphs above and retain paragraph below if generator is protected by a generator protector.

D. Generator Disconnect Switch:  Molded-case type, 100 percent rated.

1. Rating:  Matched to generator output rating.

2. Shunt Trip:  Connected to trip switch when signaled by generator protector or by other protective devices.

Protection scheme specified in paragraph below may be proprietary.  Consult manufacturers.

E. Generator Protector:  Microprocessor-based unit that continuously monitors current level in each phase of generator output, integrates generator heating effect over time, and predicts when thermal damage of the alternator will occur.  When signaled by the protector or other generator-set protective devices, a shunt-trip device in the generator disconnect switch shall open the switch to disconnect the generator from the load circuits.  Protector performs the following functions:

1. Initiates a generator overload alarm when the generator has operated at an overload equivalent to 110 percent of full-rated load for 60 seconds.  Indication for this alarm is integrated with other generator-set malfunction alarms.

2. Under single or three-phase fault conditions, regulates the generator to 300 percent of rated full-load current for up to 10 seconds.

3. As heating effect on the generator of overcurrent approaches the thermal damage point of the unit, the protector switches the excitation system off, opens the generator disconnect switch, and shuts down the generator set.

4. Senses clearing of a fault by other overcurrent devices and controls recovery of rated voltage to avoid overshoot.

Retain below for legally required emergency generator sets rated 1000 a and more at 277/480 V.  Coordinate with Drawings.

F. Ground-Fault Indication:  Comply with NFPA 70, Article 700-7(d).  Integrate ground-fault alarm indication with other generator-set alarm indications.

2.15 GENERATOR, EXCITER, AND VOLTAGE REGULATOR

A. Comply with NEMA MG 1 and specified performance requirements.

B. Drive:  Generator shaft is directly connected to engine shaft.  Exciter is rotated integrally with generator rotor.

C. Electrical Insulation:  Class H or Class F.

D. Stator-Winding Leads:  Brought out to terminal box to permit future reconnection for other voltages if required.

E. Construction prevents mechanical, electrical, and thermal damage due to vibration, overspeed up to 125 percent of rating, and heat during operation at 110 percent of rated capacity.

Coordinate paragraph below with one of two generator-set performance articles selected above.

F. Excitation uses no slip or collector rings, or brushes, and is arranged to sustain generator output under short-circuit conditions as specified.

G. Enclosure:  Dripproof.

Delete paragraph below for systems where instrument transformers are housed in control and power panel.

H. Instrument Transformers:  Mounted within generator enclosure.

I. Voltage Regulator:  Solid-state type, separate from exciter, providing performance as specified.

1. Adjusting rheostat on control and monitoring panel provides plus or minus 5 percent adjustment of output- voltage operating band.

Delete paragraph below if not required.

J. Strip Heater:  Thermostatically controlled unit arranged to maintain stator windings above dew point.

Delete two paragraphs below except for units specified for "critical" performance.  Coordinate with one of two generator-set performance articles selected above.  See Evaluations.

K. Windings:  Two-thirds pitch stator winding and fully linked amortisseur winding.

Below may require generator to be oversized for the engine driving it.  See Evaluations.

L. Subtransient Reactance:  12 percent, maximum.

2.16 ELECTRIC MOTORS

Delete this Article except for installations using remote radiators.

A. Comply with Division 15 Section "Motors."

2.17 LOAD BANK

Delete this Article if not required or revise to require resistive load elements only or another type of load bank.  Revise capacity to suit Project.  See Editing Instruction No. 11 in the Evaluations.  Coordinate with Drawings.

A. Description:  Permanent, outdoor, weatherproof, remote-controlled, forced-air-cooled, resistive and reactive unit capable of providing a balanced three-phase, delta-connected load to generator set at 100 percent rated-system capacity, at 80 percent power factor, lagging.  Unit may be composed of separate resistive and reactive load banks controlled by a common control panel.  Unit is capable of selective control of load in 25 percent steps with minimum step changes of approximately 5 and 10 percent available.

B. Resistive Load Elements:  Corrosion-resistant chromium alloy with ceramic and steel supports.  Elements are double insulated and designed for repetitive on-off cycling.  Elements are mounted in removable aluminized-steel heater cases.

C. Reactive Load Elements:  Epoxy-encapsulated reactor coils.

D. Load-Bank Heat Dissipation:  Integral fan with totally enclosed motor provides uniform cooling airflow through load elements.  Airflow and coil operating current are such that, at maximum load, with ambient temperature at the upper end of the specified range, load-bank elements operate at not more than 50 percent of maximum continuous temperature rating of the resistance wire.

E. Load Element Switching:  Remote-controlled contactors switch groups of load elements.  Contactor coils are rated 120 V.  Contactors are located in a separate NEMA 250, Type 3R enclosure within load-bank enclosure, accessible from exterior through hinged doors with tumbler locks.

F. Contactor Enclosures:  Heated by thermostatically controlled strip heaters to prevent condensation.

G. Load-Bank Enclosures:  NEMA 250, Type 3R, complying with NEMA ICS 6.  Louvers at cooling air intake and discharge openings prevent entry of rain and snow.  Openings for airflow are screened with 1/2-inch- (13-mm-) square galvanized steel mesh.  Reactive load bank includes automatic shutters at air intake and discharge.

H. Protective Devices:  Power input circuits to load banks are fused, and fuses are selected to coordinate with generator circuit breaker.  Fuse blocks are located in contactor enclosure.  Cooling airflow and overtemperature sensors automatically shut down and lock out load bank until manually reset.  Safety interlocks on access panels and doors disconnect load power, control, and heater circuits.  Fan motor is separately protected by overload and short-circuit devices.  Short-circuit devices are noninterchangeable fuses with 200,000-A interrupting capacity.

Coordinate two paragraphs below with Drawings.

I. Remote-Control Panel:  Separate from load bank in a NEMA 250, Type 1 enclosure.  Includes a control power switch and pilot light, and switches controlling groups of load elements.

Delete below if load bank is not used in automatic exercising of generator.  If load bank is used for automatic exercising, coordinate with Section covering remote-controlled switch, contactor, or electrically operated circuit breaker used to switch load bank to generator output.  Switching device is normally not part of equipment specified in this Section.

J. Control Sequence:  Control panel may be preset for adjustable single-step loading of generator during automatic exercising.

2.18 OUTDOOR GENERATOR-SET ENCLOSURE

Select one of two paragraphs below to define basic outdoor-enclosure type.  Edit below to specify enclosure features required.  Coordinate with Drawings.

A. Description:  Vandal-resistant, weatherproof steel housing, wind resistant up to 100 mph (160 km/h).  Multiple panels are lockable and provide adequate access to components requiring maintenance.  Panels are removable by one person without tools.  Instruments and control are mounted within enclosure.

Coordinate paragraph below with Drawings showing features, construction details, and equipment arrangement.

B. Description:  Prefabricated or preengineered walk-in enclosure with the following features:

1. Construction:  Galvanized steel, metal-clad, integral structural-steel-framed building erected on concrete foundation.

Revise wind speed below to suit local conditions.

2. Structural Design and Anchorage:  Adequate to resist loads imposed by 100-mph (160-km/h) wind.

3. Other structural loads, including roof, seismic, and auxiliary loads, are as indicated.

4. Space Heater:  Thermostatically controlled operating at one-half or less of rated voltage sized to prevent condensation.

5. Louvers:  Equipped with insect/rodent screen and filter arranged to permit air circulation when engine is not running while excluding exterior dust and rodents.

6. Hinged Doors:  With padlocking provisions.

Expand subparagraph below if forced ventilation rather than convection ventilation is required.

7. Ventilation:  Louvers equipped with insect/rodent screen and filter arranged to permit air circulation while excluding exterior dust and rodents.

8. Thermal Insulation:  As required to maintain winter interior temperature within limits required by components.

9. Finish:  Two-coat enamel finish over cleaned and primed surfaces.

Delete one of two paragraphs below.

C. Muffler Location:  Within enclosure.

D. Muffler Location:  External to enclosure.

E. Engine Cooling Airflow through Enclosure:  Adequate to maintain temperature rise of system components within required limits when unit operates at 110 percent of rated load for two hours with ambient temperature at top of range specified in system service conditions.

F. Louvers:  Fixed-engine cooling air inlet and discharge.  Louvers prevent entry of rain and snow.

Delete three paragraphs below if not required.

G. Automatic Dampers:  At engine cooling air inlet and discharge.  Dampers are closed to reduce enclosure heat loss in cold weather when unit is not operating.

Coordinate two paragraphs below with Drawings for supply circuits.

H. Interior Lights:  With switch.  Factory-wired, vaporproof-type fixtures within housing; arranged to illuminate controls and accessible interior.  Arrange for external circuit supply.

I. Convenience Outlets:  Factory wired.  Arrange for external circuit supply.

2.19 FINISHES

A. Indoor Enclosures and Components:  Manufacturer's standard enamel over corrosion-resistant pretreatment and compatible standard primer.

B. Outdoor Enclosures:  Manufacturer's standard enamel over corrosion-resistant pretreatment and compatible standard primer.

2.20 SOURCE QUALITY CONTROL

A. Factory Tests:  Include prototype testing and Project-specific equipment testing (testing of equipment manufactured specifically for this Project).

B. Prototype Testing:  Performed on a separate engine generator set using same engine model, constructed of identical or equivalent components and equipped with identical or equivalent accessories.

Consider requiring level 1 compliance below for other than level 1 installations to obtain benefits of specific standard requirements.

1. Tests:  Comply with those required for Level 1 energy converters in Paragraphs 3.2.1, 3.2.1.1, and 3.2.1.2 of NFPA 110.

2. Generator Tests:  Comply with IEEE 115.

3. Components and Accessories:  Items furnished with installed unit that are not identical to those on tested prototype have been tested to demonstrate compatibility and reliability.

C. Project-Specific Equipment Tests:  Factory test engine generator set and other system components and accessories before shipment.  Perform tests at rated load and power factor.  Include the following tests.

1. Full load run.

2. Maximum power.

3. Voltage regulation.

4. Transient and steady-state governing.

5. Single-step load pickup.

6. Safety shutdown.

D. Observation of Factory Tests:  Provide 14 days' advance notice of tests and opportunity for observation of test by Owner's representatives.

Coordinate below with Part 1 of this Section.

E. Report factory test results within 10 days of completion of test.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas, equipment foundations, and conditions, with Installer present, for compliance with requirements for installation and other conditions affecting packaged engine generator performance.

1. Proceed with installation only after unsatisfactory conditions have been corrected.

B. Examine roughing-in of cooling-system piping systems and electrical connections.  Verify actual locations of connections before packaged engine generator installation.

3.2 CONCRETE BASES

Coordinate sizes and locations of concrete bases.  Verify structural requirements with structural engineer.

A. Install concrete bases of dimensions indicated for packaged engine generators.  Refer to Division 3 Section "Cast-in-Place Concrete" and Division 16 Section "Basic Electrical Materials and Methods."

3.3 INSTALLATION

A. Comply with packaged engine generator manufacturers' written installation and alignment instructions, and with NFPA 110.

B. Set packaged engine generator set on concrete bases.

1. Support generator-set mounting feet on rectangular metal blocks and shims or on metal wedges having small taper, at points near foundation bolts to provide 3/4- to 1-1/2-inch (19- to 38-mm) gap between pump base and foundation for grouting.

2. Adjust metal supports or wedges until generator is level.

C. Install packaged engine generator to provide access, without removing connections or accessories, for periodic maintenance.

Delete two paragraphs below if shown on mechanical Drawings and specified in Division 15 Sections.

D. Install cooling-system piping, accessories, hangers and supports, and anchors for complete installation.

1. Extend drain piping from heat exchangers to point of disposition.

E. Install exhaust-system piping for diesel engines.  Extend to point of termination outside structure.  Size piping according to manufacturer's written instructions.

Delete paragraph below except for long horizontal exhaust piping.

F. Install condensate drain piping for diesel-engine exhaust system.  Extend drain piping from low points of exhaust system and from muffler to condensate traps and to point of disposition.

Delete paragraph below if flow-measuring systems are not specified.

G. Install flow meters and sensors where indicated.  Install flow-measuring system components and make connections according to manufacturer's written instructions.

H. Electrical Wiring:  Install electrical devices furnished by equipment manufacturers but not specified to be factory mounted.

1. Verify that electrical wiring is installed according to manufacturers' submittal and installation requirements in Division 16 Sections.  Proceed with equipment startup only after wiring installation is satisfactory.

3.4 CONNECTIONS

A. Piping installation requirements are specified in Division 15 Sections.  Drawings indicate general arrangement of piping and specialties.  The following are specific connection requirements:

1. Install piping adjacent to packaged engine generator to allow service and maintenance.

2. Connect water supply to cooling system.

3. Connect cooling-system water supply and drain piping to diesel-engine heat exchangers.  Install flexible connectors at connections to engine generator and remote radiator.

4. Connect exhaust-system piping to diesel engines.

B. Electrical wiring and connections are specified in Division 16 Sections.

C. Ground equipment.

1. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.5 IDENTIFICATION

Revise below if Division 16 Section "Basic Electrical Materials and Methods" specifies electrical identification.

A. Identify system components according to Division 15 Section "Mechanical Identification" and Division 16 Section "Electrical Identification."

3.6 FIELD QUALITY CONTROL

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect field-assembled components and equipment installation, including piping and electrical connections, and to assist in testing.  Report results in writing.

Retain one of three paragraphs below.  Coordinate this paragraph with related requirement in "Quality Assurance" Article.

If retaining first paragraph, delete remainder of Article.

B. Testing:  Owner will engage a qualified testing agency to perform field quality-control testing.

C. Testing:  Engage a qualified independent testing agency to perform field quality-control testing.

D. Testing:  Perform field quality-control testing under the supervision of the manufacturer's factory-authorized service representative.

E. Tests:  Include the following:

Revise below to suit Project.

1. Tests recommended by manufacturer.

2. InterNational Electrical Testing Association Tests:  Perform each visual and mechanical inspection and electrical and mechanical test stated in NETA ATS for emergency engine generator sets, except omit vibration baseline test.  Certify compliance with test parameters for tests performed.

3. NFPA 110 Acceptance Tests:  Perform tests required by NFPA 110 that are additional to those specified here including, but not limited to, the following:

a. Single-step full-load pickup test.

4. Battery Tests:  Measure charging voltage and voltages between available battery terminals for full-charging and float-charging conditions.  Check electrolyte level and specific gravity under both conditions.  Test for contact integrity of all connectors.  Perform an integrity load test and a capacity load test for the battery.  Verify acceptance of charge for each element of battery after discharge.  Verify measurements are within manufacturer's specifications.

5. Battery-Charger Tests:  Verify specified rates of charge for both equalizing and float-charging conditions.

6. System Integrity Tests:  Methodically verify proper installation, connection, and integrity of each element of engine generator system before and during system operation.  Check for air, exhaust, and fluid leaks.

Delete subparagraph below for short, unrestricted exhaust systems.

7. Exhaust-System Back-Pressure Test:  Use a manometer with a scale exceeding 40 inches wg (120 kPa).  Connect to exhaust line close to engine exhaust manifold.  Verify that back pressure at full-rated load is within manufacturer's written allowable limits for the engine.

Check local requirements and delete subparagraph below for most projects.  Few jurisdictions require this test for emergency or standby generator sets.

8. Exhaust Emissions Test:  Comply with applicable government test criteria.

9. Voltage and Frequency Transient Stability Tests:  Use recording oscilloscope to measure voltage and frequency transients for 50 and 100 percent step-load increases and decreases, and verify that performance is as specified.

10. Harmonic-Content Tests:  Measure harmonic content of output voltage under 25 percent and at 100 percent of rated linear load.  Verify that harmonic content is within specified limits.

Delete below except for projects subject to unwanted or illegal generator-set noise intrusion into adjacent properties or activities.  Coordinate with Drawings and with requirements of Parts 1 and 2 of this Section.

11. Noise Level Tests:  Measure A-weighted level of noise emanating from generator-set installation, including engine exhaust and cooling-air intake and discharge, at [four] <insert number> locations [on the property line] <Insert location for measurement>, and compare measured levels with required values.

F. Coordinate tests with tests for transfer switches and run them concurrently.

G. Retest:  Correct deficiencies identified by tests and observations and retest until specified requirements are met.

H. Report results of tests and inspections in writing.  Record adjustable relay settings and measured insulation resistances, time delays, and other values and observations.  Attach a label or tag to each tested component indicating satisfactory completion of tests.

I. Test instruments shall have been calibrated within the last 12 months, traceable to standards of the National Institute for Standards and Technology, and adequate for making positive observation of test results.  Make calibration records available for examination on request.

3.7 BATTERY EQUALIZATION

A. Equalize charging of battery cells according to manufacturer's written instructions.  Record individual cell voltages.

3.8 CLEANING

A. On completion of installation, inspect system components.  Remove paint splatters and other spots, dirt, and debris.  Repair damaged finish to match original finish.  Clean components internally using methods and materials recommended by manufacturer.

3.9 DEMONSTRATION

Delete paragraph below or edit to require training that suits complexity of Project.

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain packaged engine generators as specified below:

Delete subparagraph below if no transfer switches in Project.

1. Coordinate this training with that for transfer switches.

2. Train Owner's maintenance personnel on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining equipment.

3. Review data in maintenance manuals.  Refer to Division 1 Section "Contract Closeout."

Delete subparagraph above or below depending on which Section is retained in Division 1.

4. Review data in maintenance manuals.  Refer to Division 1 Section "Operation and Maintenance Data."

5. Schedule training with Owner, through Architect, with at least seven days' advance notice.

Revise number of training hours below to suit Project.  Coordinate with Division 1 Sections.

6. Minimum Instruction Period:  Eight hours.

END OF SECTION 16231

PACKAGED ENGINE GENERATORS
16231 - 1

