Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16231 - PACKAGED ENGINE GENERATORS

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes packaged diesel-engine generator sets with the following accessory features.

Adjust list below to suit Project.

1. Battery charger.

2. Day tank.

3. Muffler.

4. Outdoor enclosure.

5. Remote annunciator.

6. Remote stop switch.

7. Starting battery.

B. See Division 15 Section "Metal Ducts" for radiator fan discharge connections.

C. See Division 16 Section "Transfer Switches" for transfer switches, containing sensors and relays to initiate automatic starting and stopping.

1.2 SUBMITTALS

A. Product Data:  For the generator set and each accessory component indicated.

B. Shop Drawings:  Include plans, elevations, sections, details of installation, and location and size of each field connection.

1. Wiring Diagrams:  Power, signal, and control wiring.

C. Certified prototype test reports.

D. Field quality-control test reports.

E. Operation and maintenance data.

1.3 QUALITY ASSURANCE

Delete first paragraph below if not required for Project.

A. Manufacturer Qualifications:  Maintain a service center capable of emergency maintenance and repairs at the Project with eight hours' maximum response time.

B. Source Limitations:  Obtain packaged engine generator and auxiliary components specified in this Section through one source from a single manufacturer.

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

D. Comply with NFPA 70.

Select one of two options in paragraph below if generator set is automatically started.  Delete paragraph for manually started units.  See Editing Instruction No. 3 in the Evaluations.

E. Comply with NFPA 110 requirements for Level  [1] [2] emergency power supply system.

Delete below except for installations with critical noise abatement requirements, particularly outdoor generator sets.  Edit to suit local situation.  Coordinate with noise reduction features included in the Project design, including those relating to cooling air intake and discharge arrangement and selection of muffler and its location and orientation as shown on Drawings.

F. Noise Emission:  Comply with [applicable state and local government requirements] <Insert other Project criteria> for maximum noise level at [adjacent property boundaries] <Insert other critical locations> due to sound emitted by generator set including engine, engine exhaust, engine cooling air intake and discharge, and other components of the installation.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Caterpillar, Inc.; Engine Div.

2. Generac Corp.

3. Kohler Co; Generator Division.

4. MagneTek, Inc.

5. Onan Corp; Industrial Business Group.

6. Penn Detroit Allison.

7. Spectrum Detroit Diesel.

8. Stewart & Stevenson Services, Inc.

9. Western Diesel Services.

10. <Insert manufacturer.>

2.2 ENGINE GENERATOR SET

A. Provide a coordinated assembly of compatible components.

B. Safety Standard:  Comply with ASME B15.1.

C. Nameplates:  Each major system component is equipped with a conspicuous nameplate of component manufacturer.  Nameplate identifies manufacturer of origin and address, and model and serial number of item.

Generator-set performance capability specified below may be appropriate for projects where generator load includes only a small percentage of sensitive electronic equipment, adjustable frequency drives, or uninterruptible power supply systems.  See Evaluations.

2.3 GENERATOR-SET PERFORMANCE

A. Steady-State Voltage Operational Bandwidth:  4 percent of rated output voltage from no load to full load.

B. Steady-State Voltage Modulation Frequency:  Less than 1 Hz.

C. Transient Voltage Performance:  Not more than 20 percent variation for 50 percent step-load increase or decrease.  Voltage recovers to remain within the steady-state operating band within three seconds.

D. Steady-State Frequency Operational Bandwidth:  0.5 percent of rated frequency from no load to full load.

E. Steady-State Frequency Stability:  When system is operating at any constant load within rated load, there are no random speed variations outside the steady-state operational band and no hunting or surging of speed.

F. Transient Frequency Performance:  Less than 5 percent variation for a 50 percent step-load increase or decrease.  Frequency recovers to remain within the steady-state operating band within five seconds.

G. Output Waveform:  At no load, harmonic content measured line-to-line or line-to-neutral does not exceed 5 percent total and 3 percent for single harmonics.  The telephone influence factor, determined according to NEMA MG 1, shall not exceed 50.

Delete paragraph below if thermal-magnetic-trip type circuit breaker is specified in "Generator Overcurrent and Fault Protection" Article.

H. Sustained Short-Circuit Current:  For a 3-phase, bolted short circuit at system output terminals, the generator and its protective devices will supply a minimum of 250 percent of rated full-load current for not less than 10 seconds and then clear the fault automatically, without damage to any generator system component.

Below requires 10-second maximum automatic start time under specific conditions and includes startup only, not load assumption.  Retain, delete, or revise to suit Project.

I. Start Time:  Comply with NFPA 110, Type 10, system requirements.

2.4 SERVICE CONDITIONS

A. Environmental Conditions:  Engine generator shall be equipped to start and operate satisfactorily under the following environmental conditions without mechanical or electrical damage or deg radation of performance capability:

Select one of two ambient temperatures below.  Select first if generator-set start time must be within NFPA 110 limits.  (First usually implies installation indoors in heated space.) Coordinate with Drawings.

1. Ambient Temperature:  5 to 40 deg C.

Coordinate subparagraph below with requirement for heater "Coolant Jacket Heater" Paragraph below.

2. Ambient Temperature:  Minus 15 to plus 40 deg C.

Delete subparagraph below for outdoor units.

3. Relative Humidity:  0 to 95 percent.

Revise altitude below to actual altitude of installation.

4. Altitude:  Sea level to 1000 feet (300 m).

2.5 ENGINE

A. Description:  [4-cycle unit with maximum piston speed of 2250 fpm (11.4 m/s)] [or] [2-cycle unit with maximum piston speed of 1725 fpm (8.8 m/s)].

B. Comply with NFPA 37.

Revise fuel grade in first paragraph below to suit local use.

C. Fuel:  Fuel oil, Grade DF-2.

D. Rated Engine Speed:  1800 rpm.

Coordinate first paragraph below with Drawings.

E. Crankcase Drain:  Arranged for complete gravity drainage to an easily removable container with no disassembly and without use of pumps or siphons or special tools or appliances.

F. Engine Fuel System:  Comply with NFPA 37.  System includes the following:

1. Main Fuel Pump:  Mounted on engine.  Pump ensures adequate primary fuel flow under starting and load conditions.

2. Relief/Bypass Valve:  Automatically regulates pressure in fuel line and returns excess fuel to source.

Delete below if not required.  NFPA 110 contains temperature requirements.  Coordinate with Drawings for electrical supply.

G. Coolant Jacket Heater:  Electric-immersion type, factory installed in coolant jacket system.  Comply with NFPA 110 requirements for Level 1 equipment.

2.6 GOVERNOR

Select governor type below consistent with steady-state and transient frequency tolerances of loads.  Coordinate with "Generator-Set Performance" Article above.  Retain first type for systems with sensitive loads.

A. Type:  [Adjustable isochronous, with speed sensing] [or] [mechanical].

2.7 ENGINE COOLING SYSTEM

Coordinate below with Drawings.  See Editing Instruction No. 6 in the Evaluations.

A. Description:  Closed loop, liquid cooled, with radiator factory mounted on engine generator-set skid and integral engine-driven coolant pump.

Revise below if aluminum core is permissible.

1. Radiator Core Tubes:  Nonferrous-metal construction other than aluminum.

2.8 FUEL SUPPLY SYSTEM

A. Comply with NFPA 30 and NFPA 37.

Fuel tanks mounted within generator-set base are available as well as freestanding day-tank units specified below.

B. Day Tank:  Comply with UL 142; listed, freestanding, factory-fabricated assembly of a fuel tank with integral, float-controlled transfer pump and the following features:

1. Containment:  Integral rupture basin, 150 percent of nominal capacity of day tank.

2. Leak Detector:  Locate in rupture basin and connect to provide audible and visual alarm in the event of day-tank leak.

Revise hours in first subparagraph below to suit Project or delete subparagraph and indicate capacity on Drawings.  Coordinate with Drawings and NFPA 110 requirements.

3. Tank Capacity:  Adequate to supply fuel to engine for an uninterrupted period of four hours' operation at 100 percent of rated power output of engine generator system without being refilled.

4. Pump Capacity:  Exceeds maximum flow of fuel drawn by engine-mounted fuel supply pump at 110 percent of rated capacity, including fuel returned from engine.

5. Low-Level Alarm Sensor: Operates alarm contacts at 75 percent of normal fuel level.

Edit first subparagraph below to suit Project or delete if not required.  Coordinate with "Control and Monitoring" Article and with Drawings.

6. High-Level Alarm Sensor:  Separate device operates alarm and redundant fuel shutoff contacts at 106 percent of normal fuel level.

7. Piping Connections:  Include fuel suction and return lines to fuel storage tank; fuel supply;  and return lines to engine, local fuel fill, vent line, overflow line, and tank drain line complete with shutoff valve.

C. Base-Mounted Fuel Oil Tank:  Factory-installed and -piped, listed unit.  Features include the following:

1. Tank level indicator.

Revise capacity below to suit Project.  Consult manufacturers regarding capacities available for size of set used on Project.

2. Capacity:  Fuel for eight hours' continuous operation at 100 percent rated power output.

3. Vandal-resistant fill cap.

Determine applicable codes and regulations, and coordinate subparagraph below with Drawings.

4. Containment Provisions:  Comply with requirements of authorities having jurisdiction.

D. Exterior Fuel Oil Piping and Remote Fuel Oil Storage Tank:  As specified in Division 2 Section "Fuel-Oil Distribution."

E. Interior Fuel Oil Piping:  As specified in Division 15 Section "Fuel Oil Piping."

2.9 ENGINE EXHAUST SYSTEM

Select one of three paragraphs below for muffler.

A. Muffler:  Critical type, sized as recommended by engine manufacturer.  Measured sound level at a distance of 10 feet (3 m) from exhaust discharge, is 85 dBA or less.

B. Muffler:  Residential type, sized as recommended by engine manufacturer.  Measured sound level at a distance of 10 feet (3 m) from exhaust discharge, is 95 dBA or less.

C. Muffler:  Industrial type, sized as recommended by engine manufacturer.  Measured sound level in the 20- to 75-Hz frequency band at a distance of 25 feet (8 m) from exhaust discharge, is 87 dBA or less.

Items in paragraphs below are required for some installations.  Delete or retain below and coordinate with Drawings.

D. Condensate Drain for Muffler:  Schedule 40, black steel pipe connected to muffler drain outlet through a petcock.

E. Connections from Engine to Exhaust System:  Flexible section of corrugated stainless-steel pipe.

F. Connection from Exhaust Pipe to Muffler:  Stainless-steel expansion joint with liners.

G. Insulation for Mufflers and Indoor Exhaust Piping:  As specified in Division 15 Section "Pipe Insulation."

H. Supports for Muffler and Exhaust Piping:  Spring hangers and all-thread rods and vibration hangers as specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

I. Exhaust Piping External to Engine:  ASTM A 53, Schedule 40, welded, black steel, with welded joints and fittings.  Refer to Division 15 Section "Basic Mechanical Materials and Methods" for basic piping installation and joint construction.  Refer to Division 15 Section "Hydronic Piping" for materials and installation requirements for exhaust piping.

2.10 COMBUSTION-AIR-INTAKE

Select heavy-duty below if filters may not be serviced as often as recommended.  If air contaminant level is excessive, consult manufacturers to determine if special filtration of combustion air is needed.

A. Description: [Standard] [Heavy]-duty, engine-mounted air cleaner with replaceable dry filter element and "blocked filter" indicator.

2.11 STARTING SYSTEM

A. Description:  [12] [24]-V electric, with negative ground and including the following items:

1. Components:  Sized so they will not be damaged during a full engine-cranking cycle with ambient temperature at maximum specified in "Environmental Conditions" Paragraph in "Service Conditions" Article above.

2. Cranking Motor:  Heavy-duty unit that automatically engages and releases from engine flywheel without binding.

Select first option in subparagraph below if system description in Part 1 specifies a Level 1 or Level 2 system per NFPA 110.  Otherwise, select second option.  See Editing Instruction No. 7 in the Evaluations.

3. Cranking Cycle:  [60 seconds] [As required by NFPA 110 for system level specified].

Select one of two options in first subparagraph below.  First complies with NFPA 110 requirements.  Second is a more conservative rule used for some industrial applications.

4. Battery:  Adequate capacity within ambient temperature range specified in "Environmental Conditions" Paragraph in "Service Conditions" Article above to provide specified cranking cycle at least [twice] [three times] without recharging.

5. Battery Cable:  Size as recommended by generator-set manufacturer for cable length and battery capacity indicated.  Include interconnecting conductors and connection accessories.

6. Battery-Charging Alternator:  Factory mounted on engine with solid-state voltage regulation and 35-A minimum continuous rating.

Coordinate first subparagraph below with Drawings.

7. Battery Charger:  Current-limiting, automatic-equalizing and float-charging type.  Unit complies with UL 1236 and includes the following features:

a. Operation:  Equalizing-charging rate of 10 A is initiated automatically after battery has lost charge until an adjustable equalizing voltage is achieved at battery terminals.  Unit then automatically switches to a lower float-charging mode and continues operating in that mode until battery is discharged again.

b. Automatic Temperature Compensation:  Adjusts float and equalizes voltages for variations in ambient temperature from minus 40 deg C to plus 60 deg C to prevent overcharging at high temperatures and undercharging at low temperatures.

c. Automatic Voltage Regulation:  Maintains output voltage constant regardless of input voltage variations up to plus or minus 10 percent.

d. Ammeter and Voltmeter:  Flush mounted in door.  Ammeter indicates charging rate.

First subparagraph below covers sensing for safety indications on control and monitoring panel.  NFPA 110 requires sensing for Level 1 systems and makes sensing optional for Level 2 systems.  Edit to suit Project.  See Editing Instruction No. 3 in the Evaluations.

e. Safety Functions:  Include sensing of abnormally low battery voltage, arranged to close contacts providing low battery voltage indication on control and monitoring panel.  Also include sensing of high battery voltage and loss of ac input or dc output of battery charger.  Either of latter conditions closes contacts that provide a battery-charger malfunction indication at system control and monitoring panel.

f. Enclosure and Mounting:  NEMA 250, Type 1, wall-mounted cabinet.

2.12 CONTROL AND MONITORING

This Article specifies the subsystem that monitors, protects, and controls the engine generator set.  See Editing Instruction No. 8 in the Evaluations. Coordinate with Drawings.

Select first paragraph below for automatically started systems, second paragraph for manually started systems.

A. Functional Description:  When the mode-selector switch on the control and monitoring panel is in the automatic position, remote-control contacts in one or more separate automatic-transfer switches initiate starting and stopping of the generator set.  When the mode-selector switch is switched to the on position, the generator set manually starts.  The off position of the same switch initiates generator-set shutdown.  When the generator set is running, specified system or equipment failures or derangements automatically shut down the generator set and initiate alarms. [ Operation of a remote emergency-stop switch also shuts down the generator set.]

B. Functional Description:  Switching on-off switch on the generator control panel to the on position starts the generator set.  The off position of the same switch initiates generator-set shutdown.  When the generator set is running, specified system or equipment failures or derangements automatically shut down the generator set and initiate alarms. [ Operation of a remote emergency-stop switch also shuts down the generator set.]

C. Configuration:  Operating and safety indications, protective devices, basic system controls, and engine gages are grouped on a common control and monitoring panel mounted on the generator set.  Mounting method isolates the control panel from generator-set vibration.

Select one of three paragraphs below to specify minimum control and monitoring panel features.  First two are for standardized panels for automatically started units.  Third is for a typical manually operated generator system.  Coordinate with Drawings.  See Editing Instruction No. 9 in the Evaluations.

D. Indicating and Protective Devices and Controls:  Include those required by NFPA 110 for a Level 1 system, and the following:

E. Indicating and Protective Devices and Controls:  Include those required by NFPA 110 for a Level 2 system, and the following:

F. Indicating and Protective Devices and Controls:  Include the following:

Retain nine items below with any paragraph above.

1. AC voltmeter.

2. AC ammeter.

3. AC frequency meter.

4. DC voltmeter (alternator battery charging).

5. Engine-coolant temperature gage.

6. Engine lubricating-oil pressure gage.

7. Running-time meter.

8. Ammeter-voltmeter, phase-selector switch(es).

9. Generator voltage adjusting rheostat.

Delete five devices below except for manually started units (not covered by NFPA 110).  Coordinate with Drawings.  See Evaluations for typical local and remote alarm indications and shutdowns.

10. Start-stop switch.

11. Overspeed shutdown device.

12. Coolant high-temperature shutdown device.

13. Coolant low-level shutdown device.

14. Oil low-pressure shutdown device.

Retain any four subparagraphs below required by Project.  Coordinate with "Starting System" Article above.

15. Fuel tank derangement alarm.

16. Fuel tank high-level shutdown of fuel supply alarm.

17. Low battery alarm.

18. Battery charger malfunction alarm.

G. Supporting Items:  Include sensors, transducers, terminals, relays, and other devices, and wiring required to support specified items.  Locate sensors and other supporting items on engine, generator, or elsewhere as indicated.  Where not indicated, locate to suit manufacturer's standard.

Delete one or both paragraphs below to suit Project or applicable codes and standards.  Evaluations discuss what will be obtained by selecting first paragraph.  Coordinate with Drawings.

H. Common Remote Audible Alarm:  Comply with NFPA 110 requirements for Level 1 systems.  Include necessary contacts and terminals in control and monitoring panel.  Locate audible device and silencing means where indicated.

Retain paragraph below for manually started systems or for automatically started systems not specified to comply with NFPA 110, Level 1, but where some remote alarm functions are needed.  Coordinate with Drawings.

I. Common Remote Audible Alarm:  Signal the occurrence of any events listed below without differentiating between event types.  Locate audible device and silencing means where indicated.  Connect so that after an alarm is silenced, clearing of initiating condition will reactivate alarm until silencing switch is reset.

Delete subparagraphs below if not required to initiate common remote audible alarm in paragraph above.  Do not list events if paragraph requiring compliance with NFPA 110 is used, because NFPA 110 specifically designates alarm events to be signaled.

1. Engine high-temperature shutdown.

2. Lube-oil low-pressure shutdown.

3. Overspeed shutdown.

4. Remote emergency-stop shutdown.

5. Engine high-temperature prealarm.

6. Lube-oil low-pressure prealarm.

7. Fuel tank low level.

Delete subparagraphs below for manually started systems.  For automatically started systems, continue list above with items selected below to suit Project.

8. Overcrank shutdown.

9. Coolant low-temperature alarm.

10. Control switch not in auto position.

11. Battery-charger malfunction alarm.

12. Battery low-voltage alarm.

Coordinate below with Drawings.

J. Remote Emergency-Stop Switch:  Flush wall-mounted, unless otherwise indicated and prominently labeled.  Push button is protected from accidental operation.

2.13 GENERATOR OVERCURRENT AND FAULT PROTECTION

Select one or more items from paragraphs below to specify disconnect switch(es) and protective devices for the generator (alternator) component of the generator set.  Coordinate with "Generator-Set Performance" Article above.  See Editing Instruction No. 10 in the Evaluations.

Consider retaining first paragraph for units smaller than 200 kW where budget constraints are severe.  However, device provides little or no generator protection and no selectivity with downstream circuit protective devices.

A. Generator Circuit Breaker:  Molded-case, thermal-magnetic type; 100 percent rated; complying with NEMA AB 1 and UL 489.

1. Tripping Characteristic:  Designed specifically for generator protection.

2. Trip Rating:  Matched to generator rating.

3. Shunt Trip:  Connected to trip breaker when generator set is shut down by other protective devices.

4. Mounting:  Adjacent to or integrated with control and monitoring panel.

B. Generator Circuit Breaker:  Molded-case, electronic-trip type; 100 percent rated; complying with UL 489.

1. Tripping Characteristics:  Adjustable long-time and short-time delay and instantaneous.

2. Trip Settings:  Matched to generator thermal damage curve as closely as possible.

3. Shunt Trip:  Connected to trip breaker when generator set is shut down by other protective devices.

4. Mounting:  Adjacent to or integrated with control and monitoring panel.

Delete two paragraphs and associated subparagraphs above and retain two paragraphs and associated subparagraphs below if generator is protected by a generator protector.

C. Generator Disconnect Switch:  Molded-case type, 100 percent rated.

1. Rating:  Matched to generator output rating.

2. Shunt Trip:  Connected to trip switch when signaled by generator protector or by other protective devices.

Portions of protection scheme specified in paragraph below may be proprietary.  Consult manufacturers.

D. Generator Protector:  Microprocessor-based unit that continuously monitors current level in each phase of generator output, integrates generator heating effect over time, and predicts when thermal damage of the alternator will occur.  When signaled by the protector or other generator-set protective devices, a shunt-trip device in the generator disconnect switch shall open the switch to disconnect the generator from the load circuits.  Protector performs the following functions:

1. Initiates a generator overload alarm when the generator has operated at an overload equivalent to 110 percent of full-rated load for 60 seconds.  Indication for this alarm is integrated with other generator-set malfunction alarms.

2. Under single or three-phase fault conditions, regulates the generator to 300 percent of rated full-load current for up to 10 seconds.

3. As heating effect on the generator of overcurrent approaches the thermal damage point of the unit, the protector switches the excitation system off, opens the generator disconnect switch, and shuts down the generator set.

4. Senses clearing of a fault by other overcurrent devices and controls recovery of rated voltage to avoid overshoot.

2.14 GENERATOR, EXCITER, AND VOLTAGE REGULATOR

A. Comply with NEMA MG 1 and specified performance requirements.

B. Drive:  Generator shaft is directly connected to engine shaft.  Exciter is rotated integrally with generator rotor.

C. Electrical Insulation:  Class H or F.

D. Stator-Winding Leads:  Brought out to terminal box to permit future reconnection for other voltages if required.

E. Construction prevents mechanical, electrical, and thermal damage due to vibration, overspeed up to 125 percent of rating, and heat during specified intervals of operation at 110 percent of rated capacity.

Coordinate first paragraph below with "Generator-Set Performance" Article above.

F. Exciter uses no slip or collector rings, or brushes, and is arranged to sustain generator output under short-circuit conditions as specified.

G. Enclosure:  Dripproof.

H. Voltage Regulator:  Solid-state type, separate from exciter, providing performance as specified.

1. Adjusting rheostat on control and monitoring panel provides plus or minus 5 percent adjustment of output- voltage operating band.

Delete below if not required.

I. Strip Heater:  Thermostatically controlled unit arranged to maintain stator windings above dew point.

2.15 OUTDOOR GENERATOR-SET ENCLOSURE

Edit first paragraph below to specify enclosure features required.  Coordinate with Drawings.

A. Description:  Vandal-resistant, weatherproof steel housing, wind resistant up to 100 mph (160 km/h).  Multiple housing-access panels are lockable and provide adequate access to components requiring maintenance.  Panels are removable by one person without tools.  Instruments and controls are mounted within enclosure.

B. Engine Cooling Airflow through Enclosure:  Adequate to maintain temperature rise of system components within required limits when unit operates at 110 percent of rated load for 2 hours with ambient temperature at top of range specified in "Service Conditions" Article.

C. Louvers:  Fixed-engine cooling air inlet and discharge.  Louvers prevent entry of rain and snow.

Coordinate below with Drawings for supply circuit.

D. Convenience Outlet:  Factory wired.  Arrange for external circuit supply.

2.16 FINISHES

A. Description:  Manufacturer's standard enamel over corrosion-resistant pretreatment and compatible standard primer.

2.17 SOURCE QUALITY CONTROL

A. Factory Tests:  Include prototype testing and Project-specific equipment testing (testing of equipment manufactured specifically for this Project).

B. Prototype Testing:  Performed on a separate engine generator set using same engine model, constructed of identical or equivalent components and equipped with identical or equivalent accessories.

Consider requiring Level 1 compliance below for other than Level 1 installations to obtain benefits of specific standard requirements.

1. Tests:  Comply with those required for Level 1 energy converters in Paragraphs 3.2.1, 3.2.1.1, and 3.2.1.2 of NFPA 110.

C. Project-Specific Equipment Tests:  Factory test engine generator set and other system components and accessories before shipment.  Perform tests at rated load and power factor.  Include the following tests:

1. Full load run.

2. Maximum power.

3. Voltage regulation.

4. Transient and steady-state governing.

5. Single-step load pickup.

6. Safety shutdown.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Comply with packaged engine generator manufacturers' written installation and alignment instructions, and with NFPA 110.

B. Set packaged engine generator on concrete base.  Cast-in-place concrete, reinforcement, and formwork are specified in Division 3 Section "Cast-in-Place Concrete."

1. Support generator-set mounting feet on rectangular metal blocks and shims or on metal wedges having small taper, at points near foundation bolts to provide 3/4- to 1-1/2-inch (19- to 38-mm) gap between pump base and foundation for grouting.

2. Adjust metal supports or wedges until generator is level.

C. Install packaged engine generator to provide access for periodic maintenance without removing connections or accessories.

Delete paragraph below if shown on mechanical Drawings and specified in Division 15 Section.

D. Install exhaust-system piping for diesel engines.  Extend to point of termination outside structure.  Size piping according to manufacturer's written instructions.

Delete first paragraph below except for long horizontal exhaust piping runs.  Coordinate with Drawings.

E. Install condensate drain piping for diesel-engine exhaust system.  Extend drain piping from low points of exhaust system and from muffler to condensate traps and to point of disposition.

F. Electrical Wiring:  Install electrical devices furnished by equipment manufacturers but not specified to be factory mounted.

3.2 IDENTIFICATION

Revise below if Division 16 Section "Basic Electrical Materials and Methods" specifies electrical identification.

A. Identify system components according to Division 15 Section "Mechanical Identification" and Division 16 Section "Electrical Identification."

3.3 FIELD QUALITY CONTROL

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect field-assembled components and equipment installation, including piping and electrical connections, and to supervise testing.  Report results in writing.

B. Tests:  Include the following:

Revise list below to suit Project.

1. Tests recommended by manufacturer.

2. InterNational Electrical Testing Association Tests:  Perform each visual and mechanical inspection and electrical and mechanical test stated in NETA ATS for emergency engine generator sets, except omit vibration baseline test.  Certify compliance with test parameters for tests performed.

3. NFPA 110 Acceptance Tests:  Perform tests required by NFPA 110 that are additional to those specified here including, but not limited to, the following:

a. Single-step full-load pickup test.

4. Battery Tests:  Measure charging voltage and voltages between available battery terminals for full-charging and float-charging conditions.  Check electrolyte level and specific gravity under both conditions.  Test for contact integrity of all connectors.  Perform an integrity load test and a capacity load test for the battery.  Verify acceptance of charge for each element of battery after discharge.  Verify measurements are within manufacturer's specifications.

5. Battery-Charger Tests:  Verify specified rates of charge for both equalizing and float-charging conditions.

6. System Integrity Tests:  Methodically verify proper installation, connection, and integrity of each element of engine generator installation before and during system operation.  Check for air, exhaust, and fluid leaks.

Delete subparagraph below for short, unrestricted exhaust systems.

7. Exhaust-System Back-Pressure Test:  Use a manometer with a scale exceeding 40-inch wg (120 kPa).  Connect to exhaust line close to engine exhaust manifold.  Verify that back pressure at full-rated load is within manufacturer's written allowable limits for the engine.

Delete subparagraph below except for projects subject to unwanted or illegal generator-set noise intrusion into adjacent properties or activities. Coordinate with drawings and with requirements of Parts 1 and 2 of this Section.

8. Noise Level Tests:  Measure A-weighted level of noise emanating from the generator-set installation, including engine exhaust and cooling air intake and discharge, at [four] <Insert number> locations [on the property line] <Insert location for measurement>, and compare measured levels with required values.

C. Coordinate generator-set tests with tests for transfer switches and perform them concurrently.

D. Retest:  Correct deficiencies identified by tests and observations and retest until specified requirements are met.

E. Report results of tests and inspections in writing.  Record adjustable relay settings and measured insulation resistances, time delays, and other values and observations.

F. Test instruments shall have been calibrated within the last 12 months, traceable to NIST standards, and adequate for making positive observation of test results.  Make calibration records available for examination on request.

3.4 BATTERY EQUALIZATION

A. Description:  Equalize charging of battery cells according to manufacturer's written instructions.  Record individual cell voltages.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain packaged engine generators.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

1. Coordinate with training requirements for transfer switch.

END OF SECTION 16231

PACKAGED ENGINE GENERATORS
16231 - 1

