Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16264 - STATIC UNINTERRUPTIBLE POWER SUPPLY

PART 1 -  GENERAL

1.1 SUMMARY

Edit below to describe basic features of equipment for this Project.

A. This Section includes three-phase, on-line, static-type, UPS installation, complete with transient voltage surge suppression, input harmonics reduction, rectifier-charger, battery, battery disconnect device, inverter, static bypass transfer switch and the following features:

Adjust list below to suit Project.

1. Internal maintenance bypass/isolation switch.

2. Output isolation transformer.

3. Basic battery monitoring.

4. <Insert other required major features.>

1.2 SUBMITTALS

A. Product Data:  Include data on features, components, ratings, and performance for each uninterruptible power supply component indicated.

B. Shop Drawings:  Detail assemblies of equipment indicating dimensions, weights, components, and location and identification of each field connection.  Show access, workspace, and clearance requirements; details of control panels; and battery arrangement.

1. Wiring Diagrams:  Power, signal, and control wiring.

C. Field quality-control test reports.

D. Operation and maintenance data.

1.3 QUALITY ASSURANCE

Delete first paragraph below if not required or not available.

A. Manufacturer Qualifications:  A firm who maintains a service center capable of providing training, parts, and emergency maintenance and repairs for equipment at Project site with [eight hours'] <Insert time period> maximum response time.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1. UPS Units:  Listed and labeled under UL 1778.

Retain below if UPS components for this Project are installed in computer rooms.

2. Mark UPS components as suitable for installation in computer rooms according to NFPA 75.

1.4 WARRANTY

See Evaluations.

A. Special Battery Warranties:  Manufacturer's standard form in which manufacturer and Installer agree to replace UPS system storage batteries that fail in materials or workmanship within specified warranty period.

Select one of two subparagraphs below to specify typical industry UPS battery life warranty for type of battery specified in Part 2.  Consult manufacturers' literature and edit, if desired, to suit Project.  See Evaluations.

1. Warranted Cycle Life for Sealed Lead-Acid Batteries:  Equal to or greater than that represented in manufacturer's published table, including figures corresponding to the following, based on annual average battery temperature of 77 deg F (25 deg C):

Discharge Rate
Discharge Duration
Discharge End Voltage
Cycle Life






8 hours
8 hours
1.67
6 cycles

30 minutes
30 minutes
1.67
20 cycles

15 minutes
1 minute
1.67
120 cycles

2. Warranted Cycle Life for Premium Sealed Lead-Acid Batteries:  Equal or greater than that represented in manufacturer's published table, including figures corresponding to the following, based on annual average battery temperature of 77 deg F (25 deg C):

Discharge Rate
Discharge Duration
Discharge End Voltage
Cycle Life






8 hours
8 hours
1.67
40 cycles

30 minutes
30 minutes
1.67
125 cycles

15 minutes
1 minute
1.67
750 cycles

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Alber Corp.; Hawker Siddeley.

2. Best Power; a Unit of General Signal Corp.

3. BTECH, Inc.

4. C&D Powercom; Charter Power Systems, Inc.

5. Computer Power, Inc.

6. Deltec Corporation.

7. Exide Electronics.

8. HDR Power Systems, Inc.

9. Hoppecke Battery Systems, Inc.

10. Johnson Controls, Inc.; Specialty Battery Division.

11. International Computer Power.

12. International Power Machines Corp./Exide Electronics.

13. Liebert Corp.

14. MGE-UPS Systems, Inc.

15. Mitsubishi Electric Automation Div.

16. Pacific Power Source; a Thermo Voltec Company.

17. SAFT Nife.

18. Toshiba International Corp.

19. Yuasa Exide, Inc.

20. <Insert manufacturer.>

2.2 FUNCTIONAL DESCRIPTION

A. Automatic operation includes the following:

1. Normal Conditions:  Supply the load with ac power flowing from the normal ac power input terminals, through the rectifier-charger and inverter, with the battery connected in parallel with the rectifier-charger output.

2. Abnormal Supply Conditions:  If normal ac supply deviates from specified and adjustable voltage, voltage waveform, or frequency limits, the battery supplies energy to maintain constant, regulated inverter ac power output to the load without switching or disturbance.

3. If normal power fails, energy supplied by the battery through the inverter continues supply- regulated ac power to the load without switching or disturbance.

4. When power is restored at the normal supply terminals of the system, controls automatically synchronize the inverter with the external source before transferring the load.  The rectifier-charger then supplies power to the load through the inverter and simultaneously recharges the battery.

5. If battery becomes discharged and normal supply is available, the rectifier-charger charges the battery.  On reaching full charge, the rectifier-charger automatically shifts to a float-charge mode.

6. If any element of the UPS system fails and power is available at the normal supply terminals of the system, the static bypass transfer switch switches the load to the normal ac supply circuit without disturbance or interruption of supply.

7. If a fault occurs in the system supplied by the UPS and current flows in excess of the overload rating of the UPS system, the static bypass transfer switch operates to bypass the fault current to the normal ac supply circuit for fault clearing.

8. When the fault has cleared, the static bypass transfer switch returns the load to the UPS system.

9. If battery is disconnected, the UPS continues to supply power to the load with no deg radation of its regulation of voltage and frequency of the output bus.

B. Manual operation includes the following:

Revise functional descriptions in subparagraphs below to suit Project.

1. Turning the inverter off causes the load to be transferred by the static bypass transfer switch directly to the normal ac supply circuit without disturbance or interruption.

2. Turning the inverter on causes the static bypass transfer switch to transfer the load to the inverter.

Retain paragraph and subparagraphs below if maintenance bypass/isolation switch is specified for UPS units.

C. Maintenance Bypass/Isolation Switch Operation:  Switch is interlocked so it cannot be operated unless static bypass transfer switch is in the bypass mode.  Device provides manual selection between the following three conditions without interrupting supply to the load during switching:

1. Full Isolation:  Load is supplied, bypassing the UPS.  Normal UPS ac input circuit, static bypass transfer switch, and UPS load terminals are completely disconnected from external circuits.

2. Maintenance Bypass:  Load is supplied, bypassing the UPS.  UPS ac supply terminals are energized to permit operational checking, but system load terminals are isolated from the load.

3. Normal:  Normal UPS ac supply terminals are energized and the load is supplied through either the static bypass transfer switch and UPS rectifier-charger and inverter, or the battery and the inverter.

2.3 SERVICE CONDITIONS

A. Environmental Conditions:  UPS shall be capable of operating continuously in the following environmental conditions without mechanical or electrical damage or deg radation of operating capability, except battery performance.

If battery must operate within the temperature range specified below rather than in the environment specified in the battery special warranty, special battery selection requirements may apply.  Consult battery manufacturers.

Conditions in subparagraphs below are standard for commercial UPS equipment.  A separate ambient temperature range applies for the UPS battery, and the range of temperature conditions for the battery environment stated here is greater than that required by typical special battery warranty.  If unusual service conditions for UPS equipment exist and cannot be eliminated, specify them here by editing and adding to below.  See Editing Instruction No. 2 in the Evaluations.

1. Ambient Temperature for Electronic Components:  32 to 104 deg F (0 to 40 deg C).

2. Ambient Temperature for Battery:  41 to 95 deg F (5 to 35 deg C).

3. Relative Humidity:  0 to 95 percent, noncondensing.

4. Altitude:  Sea level to 4000 feet (1220 m).

2.4 PERFORMANCE REQUIREMENTS

Edit first paragraph and subparagraphs below to specify duration of system supply.  See Editing Instruction No. 3 in the Evaluations.

A. UPS shall perform as specified in this Article while supplying rated full-load current, composed of any combination of linear and nonlinear load, up to 100 percent nonlinear load with a load crest factor of 3.0, under the following conditions or combinations of the following conditions:

1. Inverter is switched to battery source.

2. Steady-state ac input voltage deviates up to plus or minus 10 percent from nominal voltage.

3. Steady-state input frequency deviates up to plus or minus 5 percent from nominal frequency.

4. THD of input voltage is 15 percent or more with a minimum crest factor of 3.0, and the largest single harmonic component is a minimum of 5 percent of the fundamental value.

Choice of alternative performance figure in subparagraph below affects ability of UPS to maintain specified performance capability under continuous unbalanced load conditions.  Choosing a high figure may limit competition and increase cost.  Select lowest deg ree of continuous load unbalance reasonably expected to occur for this Project.

5. Load is [30] [50] [100] percent unbalanced continuously.

B. Minimum Duration of Supply:  If battery is sole energy source supplying UPS-rated full-output load current at 80 percent power factor, duration of supply is [5] [10] [15] <Insert other appropriate duration> minutes.

C. Input Voltage Tolerance:  System steady-state and transient output performance remains within specified tolerances when steady-state ac input voltage varies plus 10, minus [20] [30] percent from nominal voltage.

Insert efficiency percentages in paragraph below that are consistent with rated capacity of the UPS unit to be provided for Project.  See table of typical values in Editing Instruction No. 5 in the Evaluations.

D. Overall UPS Efficiency:  Equal to or greater than <Insert number> percent at 100 percent load, <Insert number> percent at 75 percent load, and <Insert number> percent at 50 percent load.

Insert noise values in paragraph below that are consistent with rated capacity of UPS units specified in this Section.  See table of typical values in Editing Instruction No. 6 in the Evaluations.

E. Maximum Acoustical Noise:  <Insert value,> "A" weighting, emanating from any UPS component under any condition of normal operation, measured 39 inches (1000 mm) <Insert distance> from nearest surface of component enclosure.

Selecting first option in first paragraph below may make it easier to provide good, well-coordinated overcurrent protection for UPS feeder, but may also require manufacturer to add series reactors in input circuit for some models and may increase cost.

F. Maximum Energizing Inrush Current:  [Six] [Eight] times the full-load current.

G. Maximum AC Output-Voltage Regulation for Loads up to 50 Percent Unbalanced:  Plus or minus 2 percent over the full range of battery voltage.

H. Output Frequency:  60 Hz, plus or minus 0.5 percent over the full range of input voltage, load, and battery voltage.

I. Limitation of harmonic distortion of input current to the UPS shall be as follows:

Select one of two subparagraphs below to establish maximum harmonic distortion permitted for current drawn by the UPS from its input power source.  Input-filter-type device in first subparagraph is desirable for most applications and is vital for many.  This device commands a cost premium, however.  See Evaluations for discussion.

1. Description:  Either a tuned harmonic filter or an arrangement of rectifier-charger circuits shall limit THD to [5] [10] percent, maximum, at full-rated UPS load current, for power sources with X/R ratio between 2 and 30.

Do not retain subparagraph below for a UPS with an engine-generator-set source or for a UPS with a utility source if it may result in excessive distortion of generator load current or in higher harmonic content of current drawn by facility service than is allowed by the electric utility according to IEEE 519.  See Evaluations.

2. Description:  THD is limited to a maximum of 32 percent, at full-rated UPS load current, for power sources with X/R ratio between 2 and 30.

Select first paragraph below for UPS systems with more sensitive loads, and second paragraph for systems with less-sensitive loads.  First paragraph may command a cost premium; it may also restrict competition or force some manufacturers to use an output isolation transformer with low forward transfer impedance.  See Evaluations.  Consult manufacturers.

J. Maximum Harmonic Content of Output-Voltage Waveform:  5 percent RMS total and 3 percent RMS for any single harmonic, for 100 percent rated nonlinear load current with a load crest factor of 3.0.

K. Maximum Harmonic Content of Output-Voltage Waveform:  5 percent RMS total and 3 percent RMS for any single harmonic for rated full load with THD up to 50 percent, with a load crest factor of 3.0.

First paragraph below is one way of specifying UPS overload capability.  Other methods may be used.  Consult manufacturers' data and revise below to suit Project.  Delete if overload performance is not required.

L. Minimum Overload Capacity of UPS at Rated Voltage:  125 percent of full-load rating for 10 minutes, and 150 percent for 10 seconds in all operating modes.

M. Maximum Output-Voltage Transient Excursions from Rated Value:  For the following instantaneous load changes, stated as percentages of rated full UPS load, voltage shall remain within stated percentages of rated value and recover to, and remain within, plus or minus 2 percent of that value within 100 ms:

1. 50 Percent:  Plus or minus 8 percent.

2. 100 Percent:  Plus or minus 10 percent.

3. Loss of AC Input Power:  Plus or minus 5 percent.

4. Restoration of AC Input Power:  Plus or minus 5 percent.

N. Input Power Factor:  A minimum of 0.85 lagging when supply voltage and current are at nominal rated values and UPS is supplying rated full-load current.

O. EMI Emissions:  Comply with FCC Rules and Regulations, 47 CFR 15 for Class A equipment.

2.5 SYSTEM COMPONENTS, GENERAL

A. Enclosures:  Comply with NEMA 250, Type 1, unless otherwise indicated.

B. Control Assemblies:  Mount on modular plug-ins, readily accessible for maintenance.

For guidance on surge suppressor selection below, see the Evaluations in Division 16 Section "Transient Voltage Suppression."  Most UPS installations will be in Category B situations, but each should be evaluated independently.

C. Surge Suppression:  Protect internal UPS components from surges that enter at each ac power input connection including main disconnect, static bypass transfer switch,[ and maintenance bypass/isolation] switch.  Protect rectifier-charger, inverter, controls, and output components.

1. Use factory-installed surge suppressors tested according to IEEE C62.41, Category  [B] [C].

D. UPS Cabinet Ventilation:  Redundant fans or blowers draw in ambient air near the bottom of the cabinet and discharge it near the top rear.

2.6 RECTIFIER-CHARGER

A. Capacity:  Adequate to supply the inverter during full-rated output load conditions and simultaneously recharge the battery from fully discharged condition to 95 percent of full charge within 10 times the rated discharge time for duration of supply under battery power at full load.

Feature in first paragraph below is important for optimum battery life.

B. Output Ripple:  Limited by output filtration to less than 0.5 percent of rated current, peak to peak.

C. Rectifier-Charger Control Circuits:  Immune to frequency variations within rated frequency ranges of normal and emergency power sources.

1. Response Time:  Field adjustable for maximum compatibility with local generator-set power source.

D. Battery Float-Charging Conditions:  Comply with battery manufacturer's written instructions for battery terminal voltage and charging current required for maximum battery life.

2.7 INVERTER

Select one of two paragraphs below.  Retain second if UPS may be supplied power from a standby engine-generator set.

A. Description:  Pulse-width modulated, with sinusoidal output.

B. Description:  Pulse-width modulated, with sinusoidal output.  Include a bypass phase synchronization window adjustment to optimize compatibility with local engine-generator-set power source.

2.8 STATIC BYPASS TRANSFER SWITCH

A. Description:  Solid-state switching device providing uninterrupted transfer.  A contactor or electrically operated circuit breaker automatically provides electrical isolation for the switch.

B. Switch Rating:  Continuous duty at the rated full-load current of the UPS, minimum.

2.9 BATTERY

Edit below to suit Project requirements for battery type and housing configuration.  See Editing Instruction No. 4 and discussion of battery alternatives in the Evaluations.  Coordinate with "Warranty" Article in Part 1 and with Drawings.

A. Description:  Sealed,[ premium, heavy-duty,] valve-regulated, recombinant, lead-calcium units, factory assembled in [an isolated compartment of UPS cabinet] [or] [a separate cabinet that matches the UPS cabinet] and is equipped with a battery disconnect switch.

2.10 UPS CONTROL AND INDICATION

A. Description:  Group displays, indications, and basic system controls on a common control panel on front of UPS enclosure.

B. Minimum displays, indicating devices, and controls include those in lists below.  Provide sensors, transducers, terminals, relays, and wiring required to support listed items.  Alarms include an audible signal and a visual display.

LCD messaging in subparagraph below may not be available for many models rated 10 kVA and less.

1. Indications:  [Labeled LED] [Plain-language messages on a digital LCD or LED].

Delete items below not required.  Coordinate with remote monitoring and alarm functions and with monitoring and alarm functions specified for UPS battery in other articles in this Section.  Consider deleting all items that are nonstandard with leading manufacturers in the class or size of UPS indicated.  Some may be proprietary.  Many may not be available on units at low end of capacity range covered by this Section.  Revise list to suit Project.

2. Quantitative indications shall include the following:

a. Input voltage, each phase, line to line.

b. Input current, each phase, line to line.

c. Bypass input voltage, each phase, line to line.

d. Bypass input frequency.

e. System output voltage, each phase, line to line.

f. System output current, each phase.

g. System output frequency.

h. DC bus voltage.

i. Battery current and direction (charge/discharge).

j. Elapsed time-discharging battery.

3. Basic status condition indications shall include the following:

a. Normal operation.

b. Load-on bypass.

c. Load-on battery.

d. Inverter off.

e. Alarm condition exists.

4. Alarm indications shall include the following:

a. Bypass ac input overvoltage or undervoltage.

b. Bypass ac input overfrequency or underfrequency.

c. Bypass ac input and inverter out of synchronization.

d. Bypass ac input wrong-phase rotation.

e. Bypass ac input single-phase condition.

f. Bypass ac input filter fuse blown.

g. Internal frequency standard in use.

h. Battery system alarm.

i. Control power failure.

j. Fan failure.

k. UPS overload.

l. Battery-charging control faulty.

m. Input overvoltage or undervoltage.

n. Input transformer overtemperature.

o. Input circuit breaker tripped.

p. Input wrong-phase rotation.

q. Input single-phase condition.

r. Approaching end of battery operation.

s. Battery undervoltage shutdown.

t. Maximum battery voltage.

u. Inverter fuse blown.

v. Inverter transformer overtemperature.

w. Inverter overtemperature.

x. Static bypass transfer switch overtemperature.

y. Inverter power supply fault.

z. Inverter transistors out of saturation.

aa. Identification of faulty inverter section/leg.

ab. Inverter output overvoltage or undervoltage.

ac. UPS overload shutdown.

ad. Inverter current sensor fault.

ae. Inverter output contactor open.

af. Inverter current limit.

5. Controls shall include the following:

a. Inverter on-off.

b. UPS start.

c. Battery test.

d. Alarm silence/reset.

e. Output-voltage adjustment.

6. UPS in alarm condition.

7. UPS off (maintenance bypass closed).

Of components and features listed in articles below, some are options and some are standard, depending on manufacturer, model, and rating.  For some, a single component functions as two.  See Evaluations.  Select those components required for Project.

2.11 MAINTENANCE BYPASS/ISOLATION SWITCH

Many UPS units in the 5- to 125-kVA range do not have devices specified in this Article as a standard feature.  Loads of UPS units without these devices must be shut down if UPS units are de-energized for maintenance or repair.  See Evaluations.

A. Description:  Manually operated switch or arrangement of switching devices with mechanically actuated contact mechanism arranged to route the flow of power to the load around the rectifier-charger, inverter, and static bypass transfer switch.

1. Switch shall be interlocked to prevent interrupting power to the load when switching to the bypass mode.

2. Switch shall isolate other UPS components electrically to permit safe servicing.

3. Mounting:  Internal to system cabinets.

4. Switch Rating:  Continuous duty at rated full-load current of UPS.

2.12 OUTPUT ISOLATION TRANSFORMER

This Article specifies an important feature for UPS units serving loads susceptible to conducted EMI, if there are no other provisions for adequate attenuation of EMI.  Output isolation transformers have other functions besides mitigation of EMI and may be standard on certain models by some manufacturers.  In some applications, a UPS serves loads through one or more power distribution units that contain shielded isolation transformers.  In such cases, any output transformer in the UPS does not need to meet shielding requirements in this Article.  See Evaluations.

A. Description:  [Shielded unit] [Unit] with low forward transfer impedance up to 3 kHz, minimum.  Include the following features:

Select K-factor in first subparagraph below that is appropriate for UPS load in this Project.  Consider harmonic diversity and avoid overestimating the K-factor.

1. Comply with applicable portions of UL 1561, including requirements for nonlinear load current-handling capability for a K-factor of approximately [4] [9] [13] [20].

2. Output Impedance at Fundamental Frequency:  Between 3 and 4 percent.

3. Regulation:  5 percent, maximum, at rated nonlinear load current.

4. Full-Load Efficiency at Rated Nonlinear Load Current:  96 percent, minimum.

5. Electrostatic Shielding of Windings:  Independent for each winding.

6. Coil Leads:  Physically arranged for minimum interlead capacitance.

7. Shield Grounding Terminal:  Separately mounted.  Labeled, "Shield Ground."

8. Capacitive Coupling between Primary and Secondary:  33 picofarads, maximum, over a frequency range of 20 Hz to 1 MHZ.

2.13 BASIC BATTERY MONITORING

This Article specifies optional monitoring of UPS batteries.

A. Battery Ground-Fault Detector:  Initiates alarm when resistance to ground of positive or negative bus of battery is less than 5000 ohms.

2.14 BATTERY CYCLE WARRANTY MONITOR

Retain this Article if UPS battery is covered by a cycle-life warranty specified in Part 1 and warranty requires continuous monitoring of battery cycling.

A. Description:  Electronic device, acceptable to battery manufacturer as a basis for warranty action, for monitoring of charge-discharge cycle history of batteries covered by a cycle-life warranty.

B. Basic Functional Performance:  Automatically measures and records each discharge event, classifies it according to duration category, and totals discharges according to warranty criteria, displaying remaining warranted battery life on integral LCD.

Functions below represent optional features available for battery cycle monitors.  Delete those not required or that are provided by separate UPS battery monitoring features specified in previous articles in this Section.

C. Additional monitoring functions and features shall include the following:

1. Measuring and Recording:  Total voltage at battery terminals, providing alarm for excursions outside the proper float voltage level.

2. Monitors:  Ambient temperature at battery and initiates an alarm if temperature deviates from normally acceptable range.

3. Keypad on Device Front Panel:  Provides access to monitored data using front panel display.

4. Alarm Contacts:  Arranged to provide [local] [remote] alarm for [battery discharge events] [abnormal temperature] [abnormal battery voltage or temperature].

5. Memory:  Device stores recorded data in nonvolatile electronic memory.

6. RS-232 Port:  Permits downloading data to a portable personal computer.

7. Modem:  Makes measurements and recorded data accessible to remote personal computer via telephone line.  Computer is not specified in this Section.

2.15 SOURCE QUALITY CONTROL

A. Factory test complete UPS,[ including battery,] before shipment.  Include the following tests:

1. Functional test and demonstration of all functions, controls, indicators, sensors, and protective devices.

2. Full-load test.

3. Transient-load response test.

4. Overload test.

5. Power failure test.

6. Efficiency test at 50, 75, and 100 percent of rated full-load current at rated power factor.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Set UPS on concrete base.  Cast-in-place concrete, reinforcement, and formwork are specified in Division 3 Section "Cast-in-Place Concrete."

B. Maintain minimum clearances and workspace at equipment according to manufacturer's written instructions and NFPA 70.

3.2 GROUNDING

See Evaluations for discussion of grounding for separately derived systems created by isolation transformers.  Coordinate with Drawings.

A. Comply with Division 16 Section "Grounding and Bonding" for materials and installation requirements.

B. Separately Derived Systems:  If not part of a listed power supply for a data-processing room, comply with NFPA 70 requirements and manufacturers instructions for connecting to grounding electrodes and for bonding to metallic piping near isolation transformer.

3.3 IDENTIFICATION

A. Identify components and wiring according to Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]."

3.4 BATTERY EQUALIZATION

A. Equalize charging of battery according to manufacturer's written instructions.  Record voltages.

3.5 FIELD QUALITY CONTROL

A. Manufacturer's Field Service:  Engage the services of a factory-authorized service representative to supervise installation, startup, and preliminary testing and adjustment of UPS, and to participate in final inspections, tests, and adjustments.

B. Electrical Tests and Inspections:  Perform tests and inspections according to manufacturer's written instructions and as listed below to demonstrate condition and performance of each component of the UPS:

1. Inspect interiors of enclosures, including the following:

a. Integrity of mechanical and electrical connections.

b. Component type and labeling verification.

c. Ratings of installed components.

2. Test manual and automatic operational features and system protective and alarm functions.

C. Retest:  Correct deficiencies and retest until specified requirements are met.

D. Record of Tests and Inspections:  Maintain and submit documentation of tests and inspections, including references to manufacturers' written instructions and other test and inspection criteria.  Include results of tests, inspections, and retests.

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain static UPS.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 16264

STATIC UNINTERRUPTIBLE POWER SUPPLY
16264 - 1

