Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16269 - VARIABLE FREQUENCY CONTROLLERS

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes solid-state, PWM, VFCs for speed control of three-phase, squirrel-cage induction motors.

1.2 SUBMITTALS

A. Product Data:  Provide dimensions; mounting arrangements; location for conduit entries; and manufacturer's technical data on features, performance, electrical ratings, characteristics, and finishes for each type of VFC indicated.

B. Shop Drawings:  For each VFC.

1. Include dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment.  Show tabulations of installed devices, equipment features, and ratings.  Include the following:

a. Each installed unit's type and details.

b. Nameplate legends.

c. Short-circuit current ratings of integrated unit.

Delete subparagraph below if series rating of overcurrent protective devices is not used or if VFCs are used without front-end overcurrent protective devices.

d. UL listing for series rating of overcurrent protective devices in combination controllers.

Delete first subparagraph below if combination controllers are not used.

e. Features, characteristics, ratings, and factory settings of each motor-control center unit.

2. Wiring Diagrams:  Power, signal, and control wiring.

C. Field quality-control test reports.

D. Operation and maintenance data.

Coordinate two paragraphs below with Parts 2 and 3 where bypass controllers are required.

E. Load-Current and Overload-Relay Heater List:  Compile after motors have been installed and arrange to demonstrate that selection of heaters suits actual motor nameplate full-load currents.

Select paragraph above or below if motor running overload protection is specified as part of bypass controller in Part 2.

F. Load-Current and List of Settings of Adjustable Overload Relays:  Compile after motors have been installed and arrange to demonstrate that dip switch settings for motor running overload protection suit actual motor to be protected.

1.3 QUALITY ASSURANCE

A. Source Limitations:  Obtain VFCs of a single type through one source from a single manufacturer.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

VFCs with the same functional characteristics may vary in length and depth among manufacturers.  If installation space is limited, show maximum dimensions on Drawings, ensure that equipment is available to fit, and retain first paragraph below.  Delete below if space is not a concern.

C. Product Selection for Restricted Space:  Drawings indicate maximum dimensions for VFCs, minimum clearances between VFCs, and adjacent surfaces and other items.  Comply with indicated dimensions and clearances.

D. Comply with NFPA 70.

1.4 COORDINATION

Revise two paragraphs below to refer to other Divisions, such as Division 14 for conveyor systems, if control coordination is required.

A. Coordinate features of VFCs, installed units, and accessory devices with pilot devices and control circuits to which they connect.

B. Coordinate features, accessories, and functions of each VFC and each installed unit with ratings and characteristics of supply circuit, motor, required control sequence, and duty cycle of motor and load.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. ABB Power Distribution, Inc.; ABB Control, Inc. Subsidiary.

2. Baldor Electric Company (Graham).

3. Danfoss Inc.; Danfoss Electronic Drives Div.

4. Eaton Corp.; Cutler-Hammer Products.

5. General Electrical Distribution & Control.

6. MagneTek Drives and Systems.

7. Rockwell Automation Allen-Bradley Co.; Industrial Control Group.

8. Siemens Energy and Automation; Industrial Products Division.

9. Square D Co.

10. Toshiba International Corporation.

11. <Insert manufacturer.>

2.2 VARIABLE FREQUENCY CONTROLLERS

Two paragraphs below provide a sample specification for this type of controller.  Revise to suit Project.

A. Description:  NEMA ICS 2, IGBT, PWM, VFC; listed and labeled as a complete unit and arranged to provide variable speed of a NEMA MG 1, Design B, 3-phase, [standard] [premium]-efficiency induction motor by adjusting output voltage and frequency.

B. Design and Rating:  Match load type such as fans, blowers, and pumps; and type of connection used between motor and load such as direct or through a power-transmission connection.

Retain one of three options in paragraph below or revise ratings to suit Project.

C. Output Rating:  3-phase; 6 to [60 Hz, with voltage proportional to frequency throughout voltage range] [66 Hz, with torque constant as speed changes] [120 Hz, with horsepower constant throughout speed range].

Revise first paragraph and subparagraphs below to suit Project.

D. Unit Operating Requirements:

1. Input ac voltage tolerance of [208 V, plus or minus 5 percent] [380 to 500 V, plus or minus 10 percent] [525 to 575 V, plus or minus 10 percent].

2. Input frequency tolerance of 50/60 Hz, plus or minus 6 percent.

3. Capable of driving full load without derating with:

a. Ambient Temperature:  0 to 40 deg C.

b. Humidity:  Less than 90 percent (noncondensing).

c. Altitude:  3300 feet (1000 m).

4. Minimum Efficiency:  96 percent at 60 Hz, full load.

5. Minimum Displacement Primary-Side Power Factor:  96 percent.

6. Overload Capability:  1.1 times the base load current for 60 seconds; 2.0 times the base load current for 3 seconds.

7. Starting Torque:  100 percent of rated torque or as indicated.

8. Speed Regulation:  Plus or minus 1 percent.

9. Isolated control interface to allow controller to follow control signal over an 11:1 speed range.

E. Internal Adjustability Capabilities:

1. Minimum Speed:  5 to 25 percent of maximum rpm.

2. Maximum Speed:  80 to 100 percent of maximum rpm.

3. Acceleration:  2 to a minimum of 22 seconds.

4. Deceleration:  2 to a minimum of 22 seconds.

5. Current Limit:  50 to a minimum of 110 percent of maximum rating.

Delete paragraph and subparagraphs below if not applicable.  Coordinate with Drawings and control sequences.

F. Self-Protection and Reliability Features:

Delete items below not required.

1. Input transient protection by means of surge suppressors.

2. Snubber networks to protect against malfunction due to system voltage transients.

3. Under- and overvoltage trips; inverter overtemperature, overload, and overcurrent trips.

4. Motor Overload Relay:  Adjustable and capable of NEMA 250, Class  [10] [20] [30] performance.

5. Notch filter to prevent operation of the controller-motor-load combination at a natural frequency of the combination.

6. Instantaneous line-to-line and line-to-ground overcurrent trips.

7. Loss-of-phase protection.

8. Reverse-phase protection.

9. Short-circuit protection.

10. Motor overtemperature fault.

Delete or revise first four paragraphs below to suit Project.

G. Multiple-Motor Capability:  Controller suitable for service to multiple motors and having a separate overload relay and protection for each controlled motor.  Overload relay shall shut off controller and motors served by it when overload relay is tripped.

H. Automatic Reset and Restart:  To attempt three restarts after controller fault or on return of power after an interruption and before shutting down for manual reset or fault correction.  Bidirectional autospeed search shall be capable of starting into rotating loads spinning in either direction and returning motor to set speed in proper direction, without damage to controller, motor, or load.

I. Power-Interruption Protection:  To prevent motor from re-energizing after a power interruption until motor has stopped.

J. Torque Boost:  Automatically vary starting and continuous torque to at least 1.5 times the minimum torque to insure high-starting torque and increased torque at slow speeds.

K. Motor Temperature Compensation at Slow Speeds:  Adjustable current fall-back based on output frequency for temperature protection of self-cooled fan-ventilated motors at slow speeds.

If input voltage or current distortion due to harmonic generation in controller is a concern, consult manufacturer for options available to mitigate harmonic distortion.  Options may include dc bus link reactors, isolation transformers, active and passive harmonic filters, and phase shifting transformers.  Insert requirements in paragraph below.

L. Input Line Conditioning:  <Insert requirements.>

If drive output voltage exceeds motor pulse-withstand capability, consult manufacturer for options available for conditioning output voltage.  Options may include line inductors, output limit filters, sine wave filters, and motor termination filters.  Insert filter requirements in first paragraph below.

M. VFC Output Filtering:  <Insert requirements.>

N. Status Lights:  Door-mounted LED indicators shall indicate the following conditions:

1. Power on.

2. Run.

3. Overvoltage.

4. Line fault.

5. Overcurrent.

6. External fault.

O. Panel-Mounted Operator Station:  Start-stop and auto-manual selector switches with manual speed control potentiometer and elapsed time meter.

Revise paragraph and subparagraphs below to suit Project.

P. Indicating Devices:  Meters or digital readout devices and selector switch, mounted flush in controller door and connected to indicate the following controller parameters:

1. Output frequency (Hz).

2. Motor speed (rpm).

3. Motor status (running, stop, fault).

4. Motor current (amperes).

5. Motor torque (percent).

6. Fault or alarming status (code).

7. PID feedback signal (percent).

8. DC-link voltage (VDC).

9. Set-point frequency (Hz).

10. Motor output voltage (V).

Revise or select first paragraph and subparagraphs below to suit Project, or delete if control signal interface is not required.

Q. Control Signal Interface:  Provide VFC with the following:

1. Electric Input Signal Interface:  A minimum of 2 analog inputs (0 to 10 V or 0/4-20 mA) and 6 programmable digital inputs.

2. Pneumatic Input Signal Interface:  3 to 15 psig (20 to 104 kPa).

3. Remote Signal Inputs:  Capability to accept any of the following speed-setting input signals from the BMS or other control systems:

a. 0 to 10-V dc.

b. 0-20 or 4-20 mA.

c. Potentiometer using up/down digital inputs.

d. Fixed frequencies using digital inputs.

e. RS485.

f. Keypad display for local hand operation.

4. Output Signal Interface:

a. A minimum of 1 analog output signal (0/4-20 mA), which can be programmed to any of the following:

1) Output frequency (Hz).

2) Output current (load).

3) DC-link voltage (VDC).

4) Motor torque (percent).

5) Motor speed (rpm).

6) Set-point frequency (Hz).

5. Remote Indication Interface:  A minimum of 2 dry circuit relay outputs (120-V ac, 1 A) for remote indication of the following:

a. Motor running.

b. Set-point speed reached.

c. Fault and warning indication (overtemperature or overcurrent).

d. PID high or low speed limits reached.

R. Communications:  Provide an RS485 interface allowing VFC to be used with an external system within a multidrop LAN configuration.  Interface shall allow all parameter settings of VFC to be programmed via BMS control.  Provide capability for VFC to retain these settings within the nonvolatile memory.

Not all manufacturers offer all options listed in four paragraphs below.  Coordinate with manufacturers selected.  Select options suitable for Project.

S. Manual Bypass:  Arrange magnetic contactor to safely transfer motor between controller output and bypass controller circuit when motor is at zero speed.  Controller-off-bypass selector switch sets mode and indicator lights give indication of mode selected.  Unit shall be capable of stable operation (starting, stopping, and running), with motor completely disconnected from controller (no load).

T. Isolating Switch:  Non-load-break switch arranged to isolate VFC and permit safe troubleshooting and testing, both energized and de-energized, while motor is operating in bypass mode.

U. Bypass Controller:  NEMA ICS 2, full-voltage, nonreversing enclosed controller with across-the-line starting capability in manual-bypass mode.  Provide motor overload protection under both modes of operation with control logic that allows common start-stop capability in either mode.

V. Integral Disconnecting Means:  NEMA  [AB 1, instantaneous-trip circuit breaker] [AB 1, molded-case switch] [KS 1, nonfusible switch] [KS 1, fusible switch] with lockable handle.

2.3 ENCLOSURES

NEMA 1 enclosure is normally standard.  If specialized enclosures are required, consult manufacturer and insert requirements below.

A. <Insert enclosure requirements.>

2.4 ACCESSORIES

A. Devices shall be factory installed in controller enclosure, unless otherwise indicated.

Delete two paragraphs below if not applicable.  Coordinate with Drawings.

B. Push-Button Stations, Pilot Lights, and Selector Switches:  NEMA ICS 2, heavy-duty type.

C. Stop and Lockout Push-Button Station:  Momentary-break, push-button station with a factory-applied hasp arranged so padlock can be used to lock push button in depressed position with control circuit open.

Delete first paragraph below if not required.

D. Control Relays:  Auxiliary and adjustable time-delay relays.

E. Standard Displays:

1. Output frequency (Hz).

2. Set-point frequency (Hz).

3. Motor current (amperes).

4. DC-link voltage (VDC).

5. Motor torque (percent).

6. Motor speed (rpm).

7. Motor output voltage (V).

F. Historical Logging Information and Displays:

1. Real-time clock with current time and date.

2. Running log of total power versus time.

3. Total run time.

4. Fault log, maintaining last four faults with time and date stamp for each.

Use below with three external current transformers.

G. Current-Sensing, Phase-Failure Relays for Bypass Controller:  Solid-state sensing circuit with isolated output contacts for hard-wired connection; arranged to operate on phase failure, phase reversal, current unbalance of from 30 to 40 percent, or loss of supply voltage; with adjustable response delay.

2.5 FACTORY FINISHES

Specify field-painting requirements in Division 9 Sections.  Verify compatibility of factory finishes with field-applied coats.

A. Manufacturer's standard prime-coat finish ready for field painting.

Edit below to include custom colors.  Coordinate custom-color requirements with sample submittal requirements.

B. Finish:  Manufacturer's standard <Insert color> paint applied to factory-assembled and -tested VFCs before shipping.

PART 3 -  EXECUTION

3.1 APPLICATIONS

Delete this Article or revise to suit office practice, Project, and drawing coordination.  Delete if VFCs and control devices and their types and features are delineated on Drawings.

A. Select features of each VFC to coordinate with ratings and characteristics of supply circuit and motor; required control sequence; and duty cycle of motor, drive, and load.

B. Select rating of controllers to suit motor controlled.

3.2 INSTALLATION

Delete paragraph below if not required and specify alternative anchoring.  Coordinate mounting methods with Drawings, including surface mounting requirements for small controllers.  Add requirements for special anchorage and seismic restraint, if applicable.

A. Anchor each VFC assembly to steel-channel sills arranged and sized according to manufacturer's written instructions.  Attach by bolting.  Level and grout sills flush with VFC mounting surface.

Coordinate mounting and anchoring of VFCs with drawing details.  If drawing details are explicit, delete paragraph below.

B. Install VFCs on concrete bases complying with Division 3 Section "[Cast-in-Place Concrete] <Insert Section title>."

Retain first paragraph below if seismic controls are Project requirement.  Coordinate with Drawings.

C. Comply with mounting and anchoring requirements specified in Division 16 Section "[Seismic Controls for Electrical Work] <Insert Section title>."

D. Controller Fuses:  Install fuses in each fusible switch.  Comply with requirements in Division 16 Section "[Fuses] <Insert Section title>."

3.3 IDENTIFICATION

A. Identify VFCs, components, and control wiring according to Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification] <Insert Section title>."

If specific operational procedures are required in emergency situations, specify below.  Include a detail on Drawings of information and instructions to be framed.  Delete below if not required.

B. Operating Instructions:  Frame printed operating instructions for VFCs, including control sequences and emergency procedures.  Fabricate frame of finished metal, and cover instructions with clear acrylic plastic.  Mount on front of VFC units.

3.4 CONTROL WIRING INSTALLATION

Delete this Article if not applicable or if remote control or indication is not required.

A. Install wiring between VFCs and remote devices according to Division 16 Section "[Conductors and Cables] <Insert Section title>."

B. Bundle, train, and support wiring in enclosures.

C. Connect hand-off-automatic switch and other automatic-control devices where available.

1. Connect selector switches to bypass only manual- and automatic-control devices that have no safety functions when switch is in hand position.

2. Connect selector switches with control circuit in both hand and automatic positions for safety-type control devices such as low- and high-pressure cutouts, high-temperature cutouts, and motor overload protectors.

3.5 FIELD QUALITY CONTROL

A. Prepare for acceptance tests as follows:

1. Test insulation resistance for each VFC element, bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

B. Testing:  Perform the following field quality-control testing:

Retain subparagraphs below with any of three paragraphs selected above.  Edit to suit Project.

1. Perform each electrical test and visual and mechanical inspection stated in NETA ATS, Sections 7.5, 7.6, and 7.16.  <Insert, in separate subparagraphs, other testing requirements.> Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance;  otherwise, replace with new units and retest.

For VFCs, supervision by personnel familiar with equipment, as specified in first paragraph below, is important.  Delete if not required.

C. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect field-assembled components and equipment installation, including pretesting and adjusting VFCs.

D. Test Reports:  Prepare a written report to record the following:

1. Test procedures used.

2. Test results that comply with requirements.

3. Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

3.6 ADJUSTING

Below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

A. Set field-adjustable switches and circuit-breaker trip ranges.

END OF SECTION 16269

VARIABLE FREQUENCY CONTROLLERS
16269 - 1

