Copyright 1998 AIA
MASTERSPEC
12/98


Copyright 1998, The American Institute of Architects (AIA)

SECTION 16315 - OVERHEAD ELECTRICAL DISTRIBUTION

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

Edit first paragraph below to describe Work specified in this Section.

A. This Section includes medium- [and secondary-]voltage, overhead electrical power distribution [and demolition] [and] [upgrading of existing overhead electrical power distribution].

B. Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1. Division 2 Section "Site Clearing" for clearing right of way for overhead lines.

2. Division 2 Section "Tree Protection and Trimming" for tree trimming in right of way.

3. Division 2 Section "Underground Ducts and Utility Structures" for underground raceways making connections to overhead lines.

4. Division 16 Section "Medium-Voltage Cables" for requirements for splicing and terminating conductors of self-supported, multiconductor, medium-voltage cable.

1.3 DEFINITIONS

Retain acronyms, abbreviations, and terms that remain after this Section has been edited.

A. ACSR:  Aluminum conductor, steel reinforced.

B. BIL:  Basic impulse level, stated in kilovolts.

C. Cable:  A conductor with insulation, a stranded conductor with or without insulation and other coverings (single-conductor cable), or a combination of conductors insulated from one another (multiconductor cable).

D. Conductor:  Material, usually in the form of a wire or cable, suitable for carrying electric current.

E. Insulated:  Separated from other conducting surfaces by a dielectric (including air space) that offers high resistance to the passage of current.

F. Insulator:  Insulating material in a form designed to support a conductor physically and to separate it electrically from another conductor or object.

G. RUS:  U.S. Department of Agriculture, Rural Utilities Service.

H. Sag:  The distance measured vertically from a conductor to the straight line joining its two points of support, measured at the midpoint of the span, unless otherwise indicated.

1. Final Sag:  The sag of a conductor under specified conditions of loading and temperature applied after it has been subjected, for an appreciable period, to the loading prescribed for the loading district in which it is situated, or equivalent loading, and the loading removed.  Final sag includes the effect of inelastic deformation (creep).

2. Initial Unloaded Sag:  The sag of a conductor before the application of an external load.

I. Secondary:  Conductors and components for circuits operating at the utilization voltage of 600 V or less.

J. Service:  Set of insulated conductors extending from a pole to the metering point or service entrance connection at the location of utilization of electricity.

K. Voltage:  The effective (root mean square) potential difference between any two conductors or between a conductor and ground.  Voltages are expressed in nominal values, unless otherwise indicated.  Nominal voltage of a system or circuit is the value assigned to a system or circuit of a given voltage class for the purpose of convenient designation.  The system's operating voltage may vary above or below this value.

1.4 SUBMITTALS

A. Product Data:  For conductors, poles, crossarms, insulators, and the following:

1. Switches.

2. Cutouts.

3. Reclosers.

4. Transformers.

5. Metering components.

6. Surge arresters.

7. Guy assemblies.

B. Qualification Data:  For firms and persons specified in "Quality Assurance" Article.

Delete paragraph below if not required.

C. Material Inspection Reports:  From a qualified independent inspection agency indicating compliance of wood poles and crossarms with requirements indicated.  RUS quality mark "WQC" on each item is acceptable in place of inspection as evidence of compliance.

Retain paragraph above or paragraph and subparagraphs below.

D. Material Certificates:  Signed by manufacturers certifying that each of the following items complies with requirements:

1. Wood poles.

2. Concrete poles.

3. Wood crossarms.

E. Listing Documentation:  Indicate products comply with RUS listing requirements specified in "Quality Assurance" Article.

Delete first paragraph below if fuses and recloser controls have been selected and coordinated as part of the design and are adequately described in this Section or on Drawings or if protective device coordination is specified elsewhere.  Coordinate with Part 2 "Cutouts, Switches, and Fuses" and "Reclosers" articles.

F. Time-Current Coordination Curves:  Illustrate optimum coordination of protective devices involved in the Work of this Section.

G. Field Test and Inspection Reports:  Indicate test and inspection results and compare them with specified requirements.

H. Maintenance Data:  For [switches] [reclosers] [transformers] to include in maintenance manuals specified in Division 1.

1.5 QUALITY ASSURANCE

Retain first paragraph below if concrete poles are specified and Contractor or manufacturer selects testing and inspecting agencies.

A. Concrete Pole Manufacturer Qualifications:  Certified by the Precast/Prestressed Concrete Institute as a qualified manufacturer of concrete utility poles of type and size indicated for this Project.

B. Inspection Agency Qualifications for Pole and Crossarm Inspection:  An independent agency, acceptable to authorities having jurisdiction, qualified to conduct inspections indicated.

C. Testing Agency Qualifications:  Testing agency as defined by OSHA in 29 CFR 1910.7 or a member company of the InterNational Electrical Testing Association and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

Usually retain first paragraph below if wood poles or crossarms are specified to cover treatment situations after typical field-cutting and -drilling operations.

D. Treatment Technician Qualifications for Field Treatment of Wood Poles and Crossarms:  Certified by authorities having jurisdiction over environmental protection at the location of Project for field application of chemicals required.

E. Electrical Components Normally Covered by Listing and Labeling Services:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

F. Overhead-Line Components, Devices, and Accessories:  Currently listed in RUS Informational Publication 202-1 without restriction for the intended application.

If selecting California Public Utilities Commission General Order 95 from paragraph below, change all subsequent IEEE C2 references accordingly.

G. Comply with [IEEE C2] [California Public Utilities Commission General Order 95], except where stricter requirements are indicated or where local requirements that are stricter apply.

H. Strength of Line and Line Components Selected by Contractor:  Provide grades of construction and strength required by IEEE C2 for conditions encountered at Project site for [heavy] [medium] [light] line loading, unless otherwise indicated.

1.6 DELIVERY, STORAGE, AND HANDLING

A. Comply with ANSI O5.1 for handling and storing wood poles for more than two weeks.  Do not use pointed handling tools capable of producing indentations greater than 1 inch (25 mm).

1.7 PROJECT CONDITIONS

Revise paragraph below to suit Project, or delete if no existing utilities.  Coordinate with requirements specified in Division 1 Section "Temporary Facilities and Controls" for temporary utilities.  Coordinate with Drawings.

A. Existing Utilities:  Do not interrupt utilities serving facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary utility services according to requirements indicated:

Edit first subparagraph below to suit Project.

1. Notify Architect not less than two days in advance of proposed utility interruptions.

2. Do not proceed with utility interruptions without Architect's written permission.

1.8 COORDINATION

Delete paragraph below or edit to specify coordination required for Project.

A. Coordinate with utility supplying electricity to lines specified in this Section, and [make final connections] [make arrangements for final connections by utility].

Coordinate below with service entrance provisions of facilities served by lines specified in this Section.

B. Coordinate with those responsible for [voice] [data] [video] <Insert other services involved> systems that will have cables supported by poles installed according to this Section.

1.9 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Fuses:  [One] <Insert number> additional spare fuse or fuse element for each furnished fuse or fuse element.

2. Special Tools:  [Two] <Insert number> sets of special-purpose tools required for maintenance of cutouts, switches, and reclosers, complete with tool box.

3. Padlocks:  [One] <Insert number> for each [three] <Insert number> installed, but not less than [three] <Insert number>.

4. Insulators:  [One] <Insert number> for every 10 of each type, but not less than [three] <Insert number> of each type.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1. Conductors:

a. AFC Cable Systems.

b. Alcan Cable Co.

c. BICC Cables Company.

d. Brugg Cable Inc.

e. Florida Wire & Cable, Inc.

f. General Wire & Cable Co.

g. Hendrix.

h. Kerite.

i. King Wire Inc.

j. Nokia Cables USA Inc.

k. Northern Lights Cables, Inc.

l. Okonite Co. (The).

m. Rome Cable Corp.

n. Southwire Co.

2. Connectors:

a. AB Chance Co.; Hubbell Power Systems.

b. Connector Manufacturing Co.

c. Cooper Power Systems.

d. Hubbell Anderson.

e. Hubbell Fargo Manufacturing Co., Inc.

3. Cutouts, Switches, and Fuses:

a. ABB Power T&D Co. Inc.

b. AB Chance Co.; Hubbell Power Systems.

c. Cooper Power Systems.

d. S&C Electric Co.

4. Grounding Materials:

a. AB Chance Co.; Hubbell Power Systems.

b. Apache Grounding; Nashville Wire Products.

c. Boggs Inc.

d. Dossert Corp.

e. Erico Inc.; Electrical Products Group.

f. Galvan Industries, Inc.

g. Hastings Fiber Glass Products, Inc.

h. Heary Brothers Lightning Protection Co.

i. Ideal Industries, Inc.

j. ILSCO Corp.

k. Korns Galvanizing Co., Inc.

l. Lightning Master Corp.

m. Lyncote XIT Grounding.

n. O-Z/Gedney Co.

o. Thomas & Betts Corporation; Utility Division.

p. Utilco Co.

5. Insulators:

a. AB Chance Co.; Hubbell Power Systems.

b. Florida Wire & Cable, Inc.

c. K-Line Insulators USA.

d. Lapp Insulator Co.

e. MacLean Power Systems.

f. Newell Porcelain Co.

g. Ohio Brass; Hubbell Power Systems.

h. Porcelain Products Co.

i. Sediver, Inc.

6. Metering Equipment:

a. ABB Power T&D Co. Inc.

b. GE Company.

c. Hughes Brothers, Inc.

d. Joslyn Hi-Voltage Corp.; High Voltage Equipment Division.

e. Landis & Staefa, Inc.

f. Siemens Building Technology.

7. Metering Transformers:

a. ABB Power T&D Co. Inc.

b. Andover Controls Corp.

c. GE Company.

d. Schlumberger Industries, Inc.

8. Pole-Line Hardware and Accessories:

a. AB Chance Co.; Hubbell Power Systems.

b. Aluma-Form, Inc.

c. American Metal Products, Inc.

d. Cooper Power Systems.

e. Dixie Metal Products, Inc.

f. Foresight Products, Inc.

g. Grip-Tite Mfg. Co. Inc.

h. Hughes Brothers, Inc.

i. Joslyn Hi-Voltage Corp.; High Voltage Equipment Division.

j. Korns Galvanizing Co., Inc.

k. MacLean Power Systems.

l. Midsun Group Inc.

m. National Foundry & Mfg.

n. Porcelain Products Co.

o. Thomas & Betts Corporation; Utility Division.

9. Poles, Concrete:

a. Accord Industries; Prestressed Pole Division.

b. Bayshore Concrete Products Corporation.

c. CPI Concrete Products, Inc.

d. Sherman Utility Structures, Inc.

e. Stress Crete Inc.

f. Stress/Crete, Ltd.

10. Poles, Wood:

a. Bell Lumber & Pole Co.

b. B. J. Carney & Co., Ltd.

c. Brown Wood Preserving Co.

d. GRA Services International, Inc.

e. J. H. Baxter & Co.

f. Koppers Industries, Inc.

g. McFarland Cascade.

h. Okonite Co. (The).

i. Taylor Lumber & Treating.

j. Western Red Cedar Association.

11. Reclosers:

a. ABB Power T&D Co. Inc.; Distribution Automation Equipment Division.

b. Cooper Power Systems.

c. G&W Electric Co.

d. Joslyn Hi-Voltage Corp.; High Voltage Equipment Division.

e. Lexington Reclosers.

f. Nu-Lee LLC.

12. Surge Arresters:

a. Cooper Power Systems.

b. GE Company; Transmission Systems.

c. Joslyn Manufacturing Co.

d. Ohio Brass; Hubbell Power Systems.

e. Raychem Corporation; Electrical Products Division.

13. Transformers, Distribution:

a. ABB Power T&D Co. Inc.

b. Cooper Power Systems.

c. Fortune Electric Co., Ltd.

d. GE Company/GE Prolec; Distribution Transformer.

e. Howard Industries, Inc.

f. Interstate Transformer Co. Inc.

g. Kuhlman Electric Corporation.

h. Moloney Electric; Division of Hammond Manufacturing.

i. Pioneer Power Products, Inc.

j. Transformer Network, Inc.

2.2 CONDUCTORS, CONNECTORS, AND SPLICES

Coordinate below with Drawings.  For multiconductor cable configurations, indicate number of conductors for each run on Drawings.  See Evaluations for conductor alternatives.

A. Medium-Voltage Line Conductors:  [Bare] [and] [covered], [all-aluminum (AAC), alloy 1350-H19, complying with ASTM B 230 and ASTM B 231 (ASTM B 231M)] [all-aluminum-alloy (AAAC), alloy 6201-T81, complying with ASTM B 398 (ASTM B 398M) and ASTM B 399 (ASTM B 399M)] [Aluminum Conductor, Steel Reinforced (ACSR), complying with ASTM B 232 (ASTM B 232M)] [Hard-drawn copper (CU), complying with ASTM B 1 and ASTM B 8].

Delete below if all line conductors are bare.  Corrdinate with Drawings.

1. Conductor Covering:  Ultraviolet resistant, complying with ICEA-S-70-547.  [High-density polyethylene] [Black, track-resistant, high-density polyethylene], <Insert mils (mm)> thick.

B. Self-Supported, Multiconductor, Insulated Medium-Voltage Lines:  Factory-assembled, messenger-supported type, listed under UL 1072 as sunlight-resistant Type MV cable for cable tray use.

1. Conductors:  [Aluminum, alloy 1350, complying with ASTM B 230 and ASTM B 231 (ASTM B 231M)] [Hard-drawn copper, complying with ASTM B 1 and ASTM B 8]; stranded for No. 2 AWG and larger.

2. Conductor Insulation:  [Cross-linked polyethylene (XLP), complying with NEMA WC 7] [Ethylene-propylene-rubber (EPR), complying with NEMA WC 8] <Insert another insulation>.

3. Insulation Level:  [100] [133] <Insert value> percent of rated circuit line-to-line voltage.

4. Conductor Shield:  Extruded, nonconducting, thermoset material, complying with NEMA WC 8, 18-mil (0.046-mm) minimum thickness.

5. Insulation Shield:  Include the following two components:

a. Nonmetallic conducting, material conforming to Table 4a of NEMA WC 8 and Tables 14.2 and 14.3 of UL 1072, extruded over, and free stripping from the insulation.

b. Metallic Tape Shield:  Bare copper, 5-mil (0.127-mm) minimum thickness, helically applied with a 15 percent minimum overlap.

Delete first subparagraph below if jacket is not required.

6. Conductor Jacket:  Extruded, chlorosulfonated-polyethylene-based material, complying with Section 4.4 10 of NEMA WC 8 and the thickness requirements in Table 4-6 of that standard.

7. Messenger:  [Copper-clad steel] [Composite copper and copper-clad steel].

8. Conductor Support Strap:  Copper strap, wound around conductors and messenger the full length of the cable.

C. Secondary-Voltage Line Conductors:  [Bare hard-drawn copper, complying with ASTM B 1 and ASTM B 8] [Covered hard-drawn copper, complying with ICEA S-70-547, with high-density polyethylene covering] [Neutral-supported, secondary service-drop cable].

D. Neutral-Supported, Secondary Service-Drop Cable:  Insulated conductors with bare neutral, complying with ICEA S-76-474, and using the following combination of materials:

1. Conductors and Neutral:  [Copper with copper-clad-steel neutral] [Aluminum with bare alloy 1350 aluminum neutral] [Aluminum with ACSR neutral].

2. Insulation:  [Cross-linked thermosetting polyethylene (XLP), complying with NEMA WC 7] [High-modular-weight, low-density polyethylene] [Weather-resistant polyolefin, complying with ICEA S-70-547].

E. Racked Secondary Conductors:  [Copper, insulated with cross-linked thermosetting polyethylene (XLP), complying with NEMA WC 7] <Insert conductor and insulation combination>.

F. Connectors, Splices, and Conductor Securing and Protecting Components:  Items include wire clamps, ties, conductor armor, fittings, connectors, and terminals.  Listed for the specific applications and conductor types and combinations of materials used.  Descriptions as follows for various applications:

1. Copper to Copper:  Copper alloy, complying with UL 486A.

2. Aluminum Composition to Aluminum Composition:  Aluminum alloy, complying with UL 486B.

3. Copper to Aluminum Composition:  Type designed for this purpose, complying with UL 486B.

4. Connectors and Splices for Secondary Conductors:  Listed and labeled for the conditions and materials involved in each application.

5. Taps for Medium-Voltage Line Conductors:  Hot-line clamps, screw type, with concealed threads and bare, hard-drawn copper stirrups.  Listed for the combination of materials being connected.

6. Splices under Tension:  Compression type with strength exceeding the conductors spliced.

7. Splices and Terminations for Covered Conductors:  As recommended by conductor manufacturer for conductor and covering combination and for specific materials and physical arrangement of each splice.

8. Splices and Terminations for Insulated Medium-Voltage Conductors:  Comply with requirements in Division 16 Section "Medium-Voltage Cables."

2.3 WOOD POLES

A. Description:  Comply with ANSI O5.1 and treat in conformance with AWPA C4 using one of the following preservatives:

Delete waterborne preservative alternative below in humid or termite-infested locations.

1. Creosote:  AWPA P1/P3.

2. Oil-Borne Preservatives and Petroleum:  AWPA P8 and AWPA P9.

3. Chromated Copper Arsenate Waterborne Preservative:  AWPA P5.

4. Ammoniacal Copper Arsenate Waterborne Preservative:  AWPA P5.

B. Wood Species:  [Any listed in ANSI O5.1 for which one of the above selected preservative treatments is specified in AWPA C4] <Insert selected wood species>.

C. Pole Marking Location:  10 feet (3 m) from the pole butt for poles 50 feet (15 m) long or less.

D. Factory Operations:  Machine trim poles by turning smooth, full length.  Roof, gain, and bore poles before pressure treatment.

2.4 CONCRETE POLES

See Evaluations for concrete pole applications.

A. Description:  [Reinforced] [Prestressed] [Cast] [Spun cast].

Coordinate paragraph below with submittal and certification requirements in Part 1.

B. Design:  Base design on calculation of strength required by IEEE C2 or indicated on Drawings, whichever is greater.  Design shall be suitable for installation at a location where annual temperature range is between [minus 4 deg F to plus 100 deg F (minus 20 deg C to plus 38 deg C)] <Insert design temperature range at site location>.  Include pole design for embedded attachments matching fittings, brackets, and other items installed in the field.

To avoid unnecessary design and manufacturing time, effort and cost, edit three paragraphs below to require only those features required for this specific Project.  Delete features nor required.

C. Shaft:  Hollow for poles at overhead-to-underground connections.  Provide 3-1/2-inch- (89-mm-) minimum cable raceway capacity, with [conduit elbow] [cable entry port] at base.

D. Water Absorption:  Not more than 3 percent.

E. Surface:  Smooth, hard, nonporous, and resistant to [soil acids] [road salts] [frost and freezing damage].

2.5 CROSSARMS

Wood units in paragraph below are adequate for most crossarm loading situations.  Indicate steel-angle crossarms if extra strength is required.  Coordinate with Drawings.

A. Description:  Solid-wood distribution type, complying with RUS REA Bulletin 1728H-701 for specified construction grade, and IEEE C2 for required climbing space and wire clearances.

Use flat braces below for most applications.  Ribbed, flat steel braces and steel-angle braces are available for unusually heavy loading.

B. Braces:  Galvanized, flat, ferrous units; 1/4 inch (6 mm) thick by 1-1/4 inches (30 mm) wide, minimum, with length to suit crossarm dimensions.

2.6 HARDWARE AND ACCESSORIES

A. Description:  Ferrous items include, but are not limited to, bolts, nuts, washers, crossarm gains and braces, insulator pins, anchor rods, anchors, eyebolts, staples, and transformer brackets.

For humid tropical or semitropical marine climates, revise end of subparagraph below.  Determine local experience and practice.

1. Comply with ANSI C135.1, ANSI C135.2, ANSI C135.4, ANSI C135.14, ANSI C135.17, ANSI C135.22, ANSI C135.33, and RUS Informational Publication 202-1 listings [with the exception that base material shall be malleable iron or ductile iron, and finish shall be hot-dip galvanized].

Coordinate paragraph below with Drawings.

B. Guy Strand Assemblies:  Cable and attachments, including strain insulators where indicated and if required by IEEE C2.  Assemblies shall have uniform minimum breaking strength for components of each assembly.

Coordinate subparagraphs below with Drawings.

1. Cable:  Seven strand.  [Zinc-coated steel, complying with ASTM A 475] [Aluminum-clad steel, complying with ASTM B 416] [Copper-clad steel, complying with ASTM B 228].

2. Cable Termination:  Thimble eye.

C. Anchor and Anchor-Rod Assemblies:  Hot-dip galvanized steel.

1. Anchors:  [Expanding] [Plate] [Swamp] [Power-installed screw] type.

Retain one or both subparagraphs below based on type of anchor rods used.

2. Anchor Rods for Manual Installation:  Threaded rod with integral [twin] [triple] thimble eye.

3. Anchor Rods for Power-Installed Screw Anchors:  ASTM A 53, Schedule 80 pipe, with coupling, and [twin] [triple] thimble eye.

D. Guy Markers:  Round vinyl or PVC material, [white] [yellow] color, 96 inches (2440 mm) long.  Shatter resistant at temperatures below 0 deg F (minus 18 deg C).

Coordinate paragraph below with Drawings for style, arrangement, and pole connection detail.

E. Insulator Brackets:  Hot-dip galvanized steel, style as indicated, designed to hold vertical-post- or -pin-type insulators, with [one] [two]-bolt attachment to pole.

Coordinate below with Drawings for sizing for conductor capacity.

F. Pole Riser Shields:  Galvanized steel with [boot] [backplate] [vent].

2.7 INSULATORS

For medium-voltage work, this Article and the requirement to comply with IEEE C2 in Part 1 will specify insulators with adequate flashover ratings for normal environmental conditions.  For contaminated atmospheres, including marine environments, add the specific insulator class designations or other identification from the relevant ANSI or CEA standards.  Select insulator types and classes that will provide adequate flashover resistance under local conditions.  Alternatively, schedule insulator application by ANSI designations on Drawings.  Check local practice.  See Evaluations.  Coordinate with Drawings.

A. General Description:  Units rated 6 kV and above shall be free from radio interference.

B. Porcelain insulators shall be wet-process type, complying with the following types:

1. Pin:  ANSI C29.5.

2. Line-Post:  ANSI C29.7.  Include mounting stud of length suitable for each mounting arrangement used.

3. Suspension:  ANSI C29.2.

4. Guy Strain:  ANSI C29.4.

5. Secondary Spool:  ANSI C29.3, Class 53-2.

C. Polymer-composite, fiberglass-reinforced insulators shall comply with the following:

1. Line Post:  Comply with CEA LWIG-02.

2. Dead End/Suspension:  Comply with CEA LWIG-01.

3. Guy Strain:  Fiberglass reinforced, epoxy finished.  Designed specifically for use in guy assemblies.

2.8 GROUNDING MATERIALS

A. Conductors:  No. 4 AWG, minimum; bare, annealed copper, complying with ASTM B 8, unless otherwise indicated.

B. Ground Rods:  [Copper-clad steel, complying with UL 467,] [solid stainless steel,] [sectional type,] [5/8 inch (15.9 mm)] [3/4 inch (19.1 mm)] in diameter by [96 inches (2440 mm)] [10 feet (3 m)] long.

C. Connectors:  Comply with UL 467.  [Exothermic-welded connections, provided in kit form and selected according to manufacturer's written instructions for specific types and sizes of items jointed] [heavy-duty bolted clamps] [high-conductivity pressure connectors].

D. Ground Wire Protectors:  PVC or half-round molding, [fir, pressure treated according to AWPA C25] [cypress] [cedar].

2.9 SURGE ARRESTERS

See Evaluations for various types and construction.

A. Distribution Class:  [Porcelain-enclosed] [Polymer-enclosed], gapless, metal-oxide type [with automatic-indicating type, ground-lead disconnection feature], complying with IEEE C62.11 and NEMA LA 1.

B. Intermediate Class:  [Porcelain-enclosed] [Polymer-enclosed], gapless, metal-oxide type, complying with IEEE C62.11 and NEMA LA 1.

Coordinate below with Drawings.  Delete if ratings are indicated in schedule.  See sample schedule in the Evaluations.

1. Voltage Rating:  [3] [6] [9] [10] [12] [15] [27] [30] [36] kV, [at the altitude of Project,] unless otherwise indicated.

2.10 CUTOUTS, SWITCHES, AND FUSES

Delete current ratings in this Article if indicated on Drawings.

A. Description:  Medium-voltage disconnect, protective, [and bypass] units shall be rated for the line-to-line voltage of the systems in which installed, unless higher ratings are indicated.  BIL ratings [45] [60] [75] [95] [150] [200] kV.

1. Momentary Current Rating of Switching Devices:  [20] [40] <Insert value> kA, asymmetrical at nominal system operating voltage.

Coordinate subparagraphs below with Drawings.  Delete if fuses have been selected and coordinated as part of the design and are adequately described in this Section or on Drawings or if protective device coordination is specified elsewhere.

Avoid using first subparagraph below because it may place vital design decisions in Contractor's hands without appropriate control and safeguards.

2. Fuse Characteristics:  Time-current characteristics for each set of fuses selected according to written recommendations of manufacturer of component protected by the fuses and coordinated with upstream and downstream protective devices.  Prepare time-current coordination curves according to IEEE 242 that illustrate optimum coordination of devices in this Project.

3. Interrupting Rating of Fuses:  <Insert value> symmetrical amperes at nominal system operating voltage.

B. Fuse Cutouts:  [Open] [enclosed] type, rated [100] [200]  A, continuous, complying with ANSI C37.42.

1. Fuses:  Enclosed link, Type  [K] [T], complying with ANSI C37.42.

Delete subparagraph below if fuse ratings are shown on Drawings, or edit to suit Project.

2. Fuse Current Rating:  150 percent of the transformer full-load current, unless otherwise indicated.

Retain both subparagraphs below if some cutouts are applied as switches.  Verify application and ratings with manufacturers.

3. Switching Application:  Include switch link instead of fuse.

4. Switch Current Interrupting Rating:  [Transformer magnetizing current] <Insert value>.

Delete ratings in first two paragraphs and associated subparagraphs below if shown on Drawings.  Coordinate with Drawings.

C. Fused Switches:  Single-pole, manual units.

1. Switch Rating:  [400] [600]-A RMS continuous and load-current interrupting.

2. Fuses:  Dropout-type power fuses.

D. Nonfused Switches:  Single-pole, manual units, rated [100] [200] [400] [600]-A RMS continuous.

E. Group-Operated, Load-Interrupter Switches:  [Fused] [Nonfused], three-pole, single-throw units, manually operated by handle through insulated mechanical linkage.

1. High-pressure contact type, complying with ANSI C37.32.

Coordinate first two subparagraphs below with Drawings.

2. Factory preassembled to suit specific configuration and mounting conditions for this Project.

3. Operating Handle:  Padlock equipped.

4. Current Interrupting Rating:  Equal to continuous current rating of switch.

Coordinate below with Drawings.

5. Fuses:  Nondropout power type.

2.11 RECLOSERS

Coordinate this Article with Drawings.

A. Description:  Automatic outdoor, [single] [three]-phase, [oil] [air]-insulated, [oil] [vacuum]-interrupter unit designed for pole-line application and complying with IEEE C37.60.

B. Control:  [Hydraulic] [Electronic solid-state].

C. Operating Power for Contacts:  Stored energy derived internally from source electrical line.

D. Control Power:  Internal rechargeable battery or other energy storage device.

E. Voltage Rating:  Equal to or greater than rated system voltage as recommended by manufacturer.

F. BIL Rating:  [45] [60] [75] [95] [150] [200] kV.

G. Continuous Current Rating:  <Insert value>-A RMS.

Delete one or both paragraphs below and coordinate with Part 1 "Submittals" Article and with Drawings.  Delete first if recloser control settings have been selected and coordinated as part of the design and are adequately described in this Section or on Drawings.  Delete both if protective device coordination is specified elsewhere.

Avoid using first paragraph because it may place vital design decisions in Contractor's hands without appropriate control and safeguards.

H. Minimum Tripping Time-Current Setting and Reclosure Interval:  Coordinated with upstream and downstream protective devices and selected according to IEEE 242.  Prepare time-current coordination curves that illustrate optimum coordination of devices in this Project.

I. Minimum Tripping Time-Current Setting and Reclosure Interval:  <Insert values.>

On single-phase circuit reclosers, delete three-phase trip and lockout in paragraph below.

J. Sequence of Operation:  Unit senses [phase-to-ground] [phase-to-phase] overcurrent and trips open, controlled by adjustable time-current settings, then recloses after adjustable time interval.  Capability for selecting zero, one, two, or three reclosing cycles [on individual phases], followed by lockout[, including trip and lockout, of non-faulted phases,] after last unsuccessful reclosure.

Delete optional paragraph below if not required for local or remote current reading or recording.

K. Three-Phase, Current Metering Sensors:  Integral with bushings.

Delete paragraph below except for three-phase reclosers if ground-fault relaying is included in protection scheme.

L. Ground-Fault Current Sensing:  Solid-state control relay senses ground faults by measuring the residual component of the three-phase current.

Delete paragraph below unless remote monitoring is desired and communication network access will be provided at recloser location.

M. Remote Metering and Monitoring Communication Module:  Provide analog-to-digital conversion of current and status sensing and capability for network communications as part of facility electrical power monitoring and control installation[.] [as specified in Division 16 Section "Electrical Power Monitoring and Control."]

Retain paragraph below for locations with contaminated atmosphere.  Consult manufacturers and revise to suit Project.

N. Bushings:  Creepage distance shall exceed nominal value standard for unit rating by at least 75 percent.

Retain two paragraphs below for installations in corrosive environments.

O. Hardware:  Stainless steel.

P. Tank and Cover:  Stainless steel complying with ASTM A 167, Type 304 or 304L, with paint coating exterior finish system complying with ANSI C57.12.28, including manufacturer's standard color finish coat.

2.12 DISTRIBUTION TRANSFORMERS

A. Description:  Single-phase, two-winding, [single] [two]-bushing, liquid-filled, pole-mounting distribution type; suitable for external fuse and surge suppressor protection.  Comply with RUS Specification D-10[.] [and the following additional requirements:]

Description above, without further requirements, specifies flammable, mineral-oil-based, insulating liquid.  Consider alternative insulating liquid described below for locations close to buildings, pedestrian areas, and high-fire-risk forests and grasslands.  Delete below if not applicable.

B. Insulating Liquid:  High-molecular weight, mineral-oil based, listed as less-flammable type.

C. Taps:  [Two 2.5 percent above and below] [Four 2.5 percent below], high-voltage and full-load rated.

D. Mounting Brackets:  [Single] [Double], integral; suitable for pole mounting, either individually or in cluster, or on crossarm.

E. Minimum Efficiency:  Class 1, as defined by NEMA TP 1, based on test results.

Retain paragraph below for locations with contaminated atmosphere.  Consult manufacturers and revise to suit local conditions.

F. Bushings:  Creepage distance shall exceed nominal value standard for unit rating by at least 75 percent.

Retain two paragraphs below for installations in corrosive environments.

G. Hardware:  Stainless steel.

H. Tank and Cover:  Stainless steel, complying with ASTM A 167, Type 304 or 304L, with paint coating exterior finish system complying with ANSI C57.12.28, including manufacturer's standard color finish coat.

2.13 PRIMARY METERING EQUIPMENT

A. Metering Transformers:  Outdoor current-transforming and potential transformers, designed for crossarm mounting, complying with ANSI 12.11 and IEEE C57.13, and including the following features:

1. BIL:  [45] [60] [75] [95] [150] [200] kV.

2. Secondary connection box arranged for conduit connection.

3. Potential-Transformer Voltage Rating:  [2.4] [4.16] [7.2] [12.0] [12.47] <Insert value> kV to 120-V ac, 60 Hz.

4. Potential-Transformer Accuracy Class:  Minimum 0.3 at [75-VA] <Insert value> burden.

5. Voltage Rating:  [2.4] [4.16] [7.2] [12.0] [12.47] <Insert value> kV.

6. Current Rating:  <Insert value> to 5 A.

7. Accuracy Class:  Minimum 0.2 at [50-VA] <Insert value> burden.

B. Watt-Hour Meter:  Outdoor solid-state unit, [with demand register,] [arranged for pulse initiation,] complying with ANSI  [C12.10] [C12.13], and including the following ratings and features:

1. Form:  [5A] [55] [6A] [65].

2. Element:  [2] [2-1/2] [3].

3. Voltage:  120 V.

4. Current:  2-1/2 A.

5. Frequency:  60 Hz.

6. Kilowatt-Hour Register:  Five-digit type.

7. Demand-Register Multiplier:  A quantity in even hundreds, indicated on meter face.

8. Demand-Register Interval:  [15] [30] minutes.

9. Mounting:  On matching socket, complying with ANSI C12.7, and complete with automatic current short-circuiting device.

10. Meter Test Block:  Matched to meter furnished and equipped with open knife switches designed to isolate each metering component for test.

11. Meter Cabinet:  Galvanized steel; weatherproof enclosure with pole-mounting bracket and the following features:

a. Hinged Door:  Arranged for padlocking in closed position.

b. Size:  Adequate house meter and other equipment indicated, but not less than 20 by 30 by 11 inches (510 by 760 by 280 mm) deep.

2.14 GROUNDING MATERIALS

A. Comply with Division 16 Section "Grounding and Bonding," using materials listed by RUS for the intended purpose without restriction.

2.15 PADLOCKS

Padlocks complying with ASTM F 883 are classified as "PO1" (key operated) and "PO2" (combination operated), with Grades 1 through 6 and Grade 6 being the highest quality, and with Option A:  Key is captive in cylinder when padlock is unlocked; Option B:  Removable cylinder; Option C:  Changeable combination; Option D:  Combination operated with key control; Option E:  Corrosion resistant; Option F:  Provided with nonferrous shackles; Option G:  Environmental resistant.

A. Description:  ASTM F 883, Class  [PO1] [PO2], Grade  [1] [2] [3] [4] [5] [6], Option  [A] [B] [C] [D] [E] [F] [G].

2.16 IDENTIFICATION PRODUCTS

A. Comply with Division 16 Section "Electrical Identification" for warning signs and equipment labels.

2.17 FINISHES

A. Enclosures and Metal Components without Finish Specifications:  Manufacturer's standard enamel over corrosion-resistant treatment.

2.18 SOURCE QUALITY CONTROL

A. Factory Tests:  Conduct routine tests of [transformers,] [medium-voltage switches,] [reclosers,] [and] [metering equipment] according to referenced standards.

Delete below unless required for critical projects.

B. Factory Inspections:  Engage a recognized independent timber inspection agency to inspect poles and crossarms before and after corrosion-resistant treatment and report results of inspection.

PART 3 -  EXECUTION

3.1 GENERAL INSTALLATION REQUIREMENTS

A. Install underground power and metering circuits and those indicated to be in raceway according to Division 2 Section "Underground Ducts and Utility Structures" and Division 16 Section "Medium-Voltage Cables," and make splices and terminations for those circuits according to those Sections.

B. Verify dimensions by field measurement, and identify locations of poles, guy anchors, and other features.  Also identify locations of connection to new and existing supply lines and to primary and secondary services.  Notify Architect of discrepancies and field conditions that are not indicated and that will affect installation.

C. Grounding:  Comply with Division 16 Section "Grounding and Bonding."

3.2 RIGHT-OF-WAY CLEARANCE AND TREE TRIMMING

Coordinate this Article with referenced Division 2 Sections.

A. Clear right of way according to Division 2 Section "Site Clearing."

B. Clear right of way to maintain minimum clearances required by IEEE C2, unless Drawings indicate greater clearances or greater clearances are required by state or local codes or regulations.  If no minimum requirements are mandated, maintain a minimum of 15 feet (4.5 m) on both sides horizontally and below medium-voltage conductors and 5 feet (1.5 m) on both sides horizontally and below secondary-voltage conductors.  Remove overhanging branches.

3.3 CONDUCTOR INSTALLATION, GENERAL

A. Handle and string conductors to prevent cuts, gouges, scratches, kinks, flattening, or deformation.  Remove damaged sections and splice conductors.

Coordinate two subparagraphs below with Drawings.

1. String new conductors to "initial" sag table values [indicated] [recommended by manufacturer for type and size of conductor and ruling span].

Delete subparagraph below if Project does not renovate existing lines.

2. Conductors Reinstalled or Resagged:  String to "final" sag values [indicated] [recommended by manufacturer for type and size of conductor and ruling span].

B. Connections, Splices, and Terminations:  Use kits listed for the specific type of connection and combination of materials used in the connection, or recommended for the specific use by manufacturer of material on which applied.

1. Splice Location:  Do not install within 10 feet (3 m) of a support.

2. Line Conductors and Service Drops:  Install so strength exceeds ultimate rated strength of conductor.

3. Splices and Terminations of Covered Conductors:  Comply with manufacturer's written instructions.

4. Splices and Terminations of Insulated Conductors of Self-Supported, Medium-Voltage Cable:  Comply with manufacturer's written instructions.

3.4 MEDIUM-VOLTAGE LINE CONDUCTOR INSTALLATION

Coordinate paragraph below with Drawings.

A. Application:  Install bare conductors, unless otherwise indicated.

Delete first paragraph below if aluminum or aluminum-composition conductors are not used.

B. Armor Rod:  Install to protect conductors if line conductors are supported by insulators.

C. Flat Aluminum Armor Wire:  Install to protect conductors if they are supported by, or attached to, galvanized or coated iron or steel clamps or fittings.

D. Support line conductors and taps as follows:

1. Use wire ties for conductor attachment to pin and vertical post insulators, unless otherwise indicated.

2. Install wire ties tight against conductor and insulator, and turn ends back, flat against conductor, to eliminate exposed wire ends.

3. Use wire clamps on horizontal post, dead end, and suspension insulators, unless otherwise indicated.

3.5 POLES AND CROSSARMS

Coordinate first paragraph below with Drawings.

A. Pole Orientation:  Align curve of curved wood poles with straight-line runs of three or more poles.  Align gained surfaces perpendicular to runs.

B. Elevation of Line above Grade:  Install poles with top elevation as uniform as possible and according to the following:

1. On level ground, set poles so tops of consecutive poles vary not more than 60 inches (1500 mm) in elevation.

2. Shorten wood poles by cutting off the top and make cuts to shed water and apply preservative.

C. Set poles according to the following:

1. Make pole holes vertical, uniform in diameter, and large enough to permit effective use of tamping bars all around.  Bore or excavate holes with an average diameter at grade less than twice the diameter of the pole at the same grade.

2. Use minimum depths indicated, except at locations where hole is partly or entirely in rock and if hole is not vertical or has a diameter at grade larger than two times the pole diameter at the same level; in these conditions, increase the depth of the hole by the following increments before setting the pole:

a. Poles up to 35 Feet (10.6 m) Long:  24 inches (600 mm).

b. Poles 36 to 60 Feet (11 to 18.3 m) Long:  30 inches (760 mm).

c. Poles 61 to 75 Feet (18.6 to 22.9 m) Long:  36 inches (900 mm).

3. For poles on slopes, indicated hole depth is from finished grade at lowest side of hole.

4. Set poles in alignment and plumb except at dead ends, angles, and points of extra strain; rake poles against conductor strain 1 inch (25 mm) minimum, 2 inches (51 mm) maximum, (after conductors are installed at required tension) for each 10 feet (3 m) of pole length.  Rake poles so they will not lean or bend in direction of strain when loaded.

5. Backfill holes in 6-inch (150-mm) maximum lifts, and thoroughly tamp each layer before starting the next.

6. Place surplus earth around pole in a conical shape, and tamp thoroughly to provide drainage away from pole.

7. Set poles so alternate crossarm gains face in alternate directions, except at terminals and dead ends; place gains on last two poles on side facing terminal or dead end.

Retain subparagraph below where applicable for projects in Seismic Zones 3 and 4.

8. Poles Set in Concrete Paved Areas:  Install poles with minimum of 6-inch- (150-mm-) wide, unpaved gap between the pole and the edge of adjacent concrete slab.  Fill unpaved ring with [pea gravel] <Insert other appropriate material> to a level 1 inch (25 mm) below top of concrete slab.

D. Field-treat factory-treated poles and crossarms as follows:

1. Poles Treated More Than One Year before Installation:  Treat portion from 24 inches (600 mm) above ground line to butt.

2. Field-Bored Holes and Field-Cut Gains and Pole Tops:  Treat cut portions.

3. Unused Holes:  Treat and plug with treated-wood-dowel drive pins.

4. Engage the services of a technician certified according to Part 1 of this Section to apply treatment.  Comply with requirements in AWPA standards that govern original factory treatment for field-applied treatment chemicals and application.

E. Crossarm Installation:  Set line crossarms at right angle to line for straight runs and for angles 45 degrees and more.  Bisect angles less than 45 degrees.

1. Buck Arms:  Install at corners and junction poles, unless otherwise indicated.

2. Double Crossarms:  Install at dead ends, corners, angles, and line crossings.

3. Equipment Arms:  Locate below lines and set parallel or at right angles to them, whichever provides best climbing space.

4. Gains:  Install factory-cut or metal pole gains only.  Do not cut gains in field without specific written approval.

3.6 HARDWARE AND ACCESSORIES INSTALLATION

A. Install washers against wood and under nuts, including eyenuts and locknuts.

B. Install nuts and locknuts wrench-tight on threaded connections.

C. Install guys to resist unbalanced loads, including those developed at angles, corners, and dead ends.  Install two or more guys if a single guy will not provide adequate strength.  Install separate guys if unbalanced loads are separated by 36 inches (900 mm) or more.

Coordinate paragraph below with Drawings.

D. Protect guy strands from damage.  Replace damaged guy strands.  Install guy insulators where required to comply with IEEE C2 clearance requirements and elsewhere, where indicated.

Delete paragraph and subparagraphs below if anchor selection is based on specific survey at each guy location or where selected strength of guy assembly indicated is adequate for all conditions encountered in Project.

E. Select guy anchors having adequate strength and holding area to suit anchor load and soil conditions at location of that anchor.

1. Soil Anchors:  Align anchors in soil with guy.  Set with anchor rod pointing at guy attachment on pole and rod projecting 6 to 9 inches (150 to 230 mm) from ground.

Delete subparagraph below if only power-installed anchors are used.

Delete depth in subparagraph below if value is indicated on Drawings.

2. Rock Anchors:  Place anchors at right angles to guy, in hole drilled [12 inches (300 mm)] <Insert value> into solid rock, with rod projecting 4 to 6 inches (100 to 150 mm) from ground.

F. Install guy markers at anchor end of guys.  Clamp to guy strand or anchor at top and bottom of marker.

3.7 INSULATORS INSTALLATION

Coordinate paragraph and subparagraphs below with Drawings.

A. Medium-Voltage Line Application:  Install [pin] [post] [pin or post] type, except install suspension type at corners, angles, dead ends, and other locations where horizontal forces exceed rated values for pin or line-post-type units.

1. Install suspension insulators and hardware that have mechanical strength exceeding rated breaking strength of attached conductors.

Delete subparagraph below for projects not using armless construction.

2. Install horizontal line-post insulators for armless construction.

B. Post-Insulator Conductor Support:  Where installed horizontally and for line angles more than 15 degrees, install clamp-top conductor clamps.

C. Install spool-type insulators for secondary lines mounted on clevis attachments or secondary racks.

D. Guy Strain Type:  Install [porcelain] [fiberglass-reinforced] units.

3.8 SURGE ARRESTERS

A. Install surge arresters to protect [distribution] [metering equipment] [reclosers], [group-operated, load interrupter switches], [aerial-to-underground transitions], [and other items indicated].

Delete below if not applicable.

1. Units Installed 6000 Feet (1800 m) or More above Sea Level:  Use arresters specifically rated for this service.

3.9 CUTOUTS, SWITCHES, AND FUSES

A. Hook-Stick-Operated Switches:  Install to allow maximize safe operating access.

B. Group-Operated, Load Interrupter Switches:  Install operating handle 42 inches (1067 mm) above finished grade.

1. Locking Provisions:  Install padlock at hasp.

3.10 METERING COMPONENTS

A. Current and Voltage Transformers:  Make secondary connections to transformer connection box using [galvanized rigid steel] [intermediate metal] [PVC] conduit.

B. Meter Cabinet:  Mount on pole, 72 inches (1825 mm) above finished grade to center of cabinet.

1. Make conduit connections with raintight hubs.

2. Install metering transformer secondary leads without splices.  Train leads at sides and bottom of enclosure and secure with wire ties.

3. Install meter and meter test block within cabinet.

4. Install identical phase sequence and color-code for both potential and current leads.

5. Identify leads using designations consistent with marking on transformer terminals.

3.11 FIELD QUALITY CONTROL

Retain one of first three paragraphs and associated subparagraphs below.  Delete all and retain "Manufacturer's Field Service" Paragraph if field quality-control testing is performed by manufacturer's service representative.

A. Testing:  Owner will engage a qualified testing agency to perform the following field quality-control inspections and testing:

B. Testing:  Engage a qualified testing agency to perform the following field quality-control inspections and testing:

C. Testing:  Perform the following inspections and tests:

Retain subparagraph below with any paragraph above.

1. Furnish instruments and equipment required for tests that comply with NETA ATS.

Delete first subparagraph and associated subparagraphs below if local experience, quality of oversight during construction, or nature of Project indicate anchor testing is not necessary.

2. Guy Anchors:  Test one of each type and capacity installed[, plus additional units specifically indicated for testing].  Apply rated pull-out force in the same pull direction applied by the guy at the test location.

a. Acceptable Test Results:  Denoted by movement of less than 3/8 inch (10 mm) by the holding component of the anchor in the earth or other medium in which it is installed.

b. Replace or reinstall, at Architect's option, each anchor of same type and capacity that fails this test.

3. Ground Resistance:  Comply with Division 16 Section "Grounding and Bonding."  Measure resistance of each separate grounding electrode, including pole grounds.  Also measure resistance of separate grounding electrode systems before bonding together.

a. Perform tests and obtain acceptable results before energizing any portion of electrical power distribution system.

b. Results and Follow-up:  If ground resistance for a single ground electrode or pole ground, tested individually, exceeds 25 ohms, add a ground electrode not less than 10 feet (3 m) away and interconnect with No. 2 AWG minimum bare conductor buried at least 12 inches (300 mm) below furnished grade.

4. Aerial Conductor Sag and Tension:  Observe procedures used by Contractor to verify that initial stringing sags and tensions comply with IEEE C2 and conductor manufacturer's Product Data and written recommendations.

5. Self-Supported, Medium-Voltage Cable:  After installation and while cable is isolated, after terminations are installed and before connecting or energizing, apply dc voltage between each phase conductor and grounding connections of sheath or metallic shield.  Comply with applicable NEMA WC 7 or NEMA WC 8 for method, voltage, duration, pass-fail performance, and other test criteria.  Perform other field inspections and tests recommended by manufacturer.

6. Neutral-Supported, Secondary Service Drop Cable:  Test for insulation resistance while cable is isolated, before connecting or energizing.  Minimum acceptable resistance is 100 megohms.

Delete first subparagraph below unless existing surge arresters are reused.  Do not reuse porcelain-enclosed, silicon carbide arresters 13 years old or more.

7. Existing Surge Arresters:  Disconnect and measure resistance between line and ground terminals with a megger rated 600 V or higher.  Acceptable resistance values are 300 megohms and higher.

8. New Surge Arresters, Cutouts, and Switches:  Inspect after installation and connection to wiring.  Verify that ratings and characteristics match approved submittals and comply with system requirements.  Verify that installation complies with requirements and that clearances of units and connecting wiring comply with IEEE C2 requirements.

a. Fuses and Disconnect Links:  Verify that ratings and characteristics match submittals and comply with system requirements.

b. Functional Test:  Manually operate each cutout and switch three times minimum, to verify proper operation.

c. Switches:  Verify correct contact alignment, blade penetration, travel stops, and arc interrupter operation.

d. Verify proper grounding of metallic equipment parts.

e. Group-Operated, Load Interrupter Switches:

1) Perform mechanical operator tests according to manufacturer's written instructions.

2) Test resistance to ground of parts to be energized.  Acceptable value is 200,000 megohms.

3) Perform contact-resistance test across each switch blade contact set.

f. Verify that clearances of energized parts and connecting wires comply with IEEE C2 requirements.

9. Reclosers:  Inspect after installation and connection to wiring and verify that ratings and characteristics match approved submittals and comply with system requirements.  Verify the integrity and good condition of unit.

a. Perform mechanical operation and contact alignment tests according to manufacturer's written instructions.

b. Verify tightness of accessible bolted connections.

c. Inspect for correct insulating-liquid level.

d. Perform overpotential test of vacuum contact assemblies.

e. Measure electrical contact resistance.

f. Perform overpotential test of recloser unit.

g. Test protective functions including tripping time-current characteristics.  Adjust to required settings.

h. Measure time delay for each reclosing interval and adjust to required value.

i. Verify lockout on unsuccessful reclosing.

j. Verify reset time and adjust to required value.

k. Verify instantaneous overcurrent trip and lockout and adjust to required value.

l. Sample insulating liquid and check for visual condition.  Test for dielectric breakdown voltage.

m. Verify that clearances of terminals and connecting wires comply with IEEE C2.

10. Distribution Transformers:  Inspect after installation and connection to wiring and verify that ratings and characteristics match approved submittals and comply with system requirements.  Verify the integrity and good condition of unit.

a. Inspect for physical damage, cracked insulators, leaks, tightness of connections, and overall mechanical and electrical integrity.

b. Perform preenergizing inspections and tests recommended by manufacturer.

c. Verify proper equipment grounding.

d. Verify that clearances of terminals and connecting wires comply with IEEE C2.

11. Metering Transformers:  Inspect after installation and connection to wires, and verify that ratings and characteristics match approved submittals and comply with system requirements.  Verify the integrity and good condition of unit.

a. Verify proper connections, tightness of bolted connections, and integrity of mounting provisions.

b. Verify required grounding and shorting connections.  Provide good contact.

c. Verify that clearances of terminals and connecting wires comply with IEEE C2.

d. Perform electrical tests according to manufacturer's written instructions, including insulation-resistance tests, polarity tests, and turns-ratio and ratio-verification tests.

12. Meters:  Inspect after installation and connection to wiring and verify that ratings and characteristics match approved submittals and comply with system requirements.  Verify the integrity and good condition of unit.

a. Verify tightness of electrical connections.

b. Verify accuracy at 25, 50, 75, and 100 percent of full-rated load and verify all instrument multipliers according to manufacturer's written instructions.

D. Repair or Replace Malfunctioning Units:  Retest as specified above after repairs or replacements are made.

Delete below if Project does not include distribution transformers, load interrupter switches, reclosers, or metering equipment.

E. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect and test [distribution transformers] [load interrupter switches] [reclosers] [metering equipment] installations, including electrical connections.  Report results in writing.

1. Provide instruments and equipment required for tests.

2. Operational Test:  After electrical circuits have been energized, exercise or operate units electrically to confirm proper functioning.

3. Test and adjust controls and safeties.

4. Adjust, repair, or remove malfunctioning components.  Replace removed items with new items and retest.

3.12 ADJUSTING

Delete this Article if transformer tap settings are indicated elsewhere.

A. Distribution Transformers:  Set voltage taps as directed by Architect.

3.13 CLEANING

A. After completing equipment installation, inspect equipment.  Remove spots, dirt, and debris.  Repair damaged finish to match original finish.  For distribution transformer, use tank touchup paint provided by manufacturer.

1. Clean enclosures internally, on completion of installation, according to manufacturer's written instructions.

3.14 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain reclosers.

1. Train Owner's maintenance personnel on procedures and schedules for operating, adjusting, troubleshooting, servicing, and maintaining equipment.

2. Review data in maintenance manuals.  Refer to Division 1 Section "Closeout Procedures."

Delete subparagraph above or below depending on which Section is retained in Division 1.

3. Review data in maintenance manuals.  Refer to Division 1 Section "Operation and Maintenance Data."

4. Schedule training with Owner, through Architect, with at least seven days' advance notice.

END OF SECTION 16315

OVERHEAD ELECTRICAL DISTRIBUTION
16315 - 1

