Copyright 1996 AIA
MASTERSPEC
9/96


Copyright 1996, The American Institute of Architects (AIA)

SECTION 16341 - MEDIUM-VOLTAGE SWITCHGEAR

This Section uses the term Architect.  Change this term as necessary to match the actual term used to identify the design professional as defined in the General and Supplementary Conditions.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes medium-voltage switchgear and associated auxiliary equipment.

B. Related Sections include the following:

List below only products, construction, and equipment for this Project that the reader might expect to find in this Section but are specified elsewhere.  Verify that Section title listed below is correct for this Project's Specifications because Section title may have changed since this Section was updated.

1. Division 16 Section "Medium-Voltage Cables" for cable terminations at switchgear.

1.3 SUBMITTALS

A. Product Data:  For each component, including the following:

1. Features, characteristics, and ratings of individual circuit breakers.

Retain subparagraph above or below or both.

2. Features, characteristics, and ratings of individual interrupter switches.

3. Time-current characteristic curves for overcurrent protective devices, including circuit-breaker trip devices and fusible devices.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loadings, required clearances, method of field assembly, components, and location and size of each field connection.  Include the following:

1. Nameplate legends.

2. Bus configuration with size and number of conductors in each bus run, including phase, neutral, and ground conductors of main and branch buses.

3. Current ratings of buses.

4. Short-time and short-circuit ratings of switchgear assembly.

Retain subparagraph below if equipment includes wiring.

5. Wiring Diagrams:  Detail wiring for power, signal, and control systems and differentiate between manufacturer-installed and field-installed wiring.

Retain paragraph below if Project involves unusual coordination requirements.

C. Coordination Drawings:  Floor plans showing dimensioned layout, required working clearances, and required area above and around switchgear where pipe and ducts are prohibited.  Show switchgear layout and relationships between components and adjacent structural and mechanical elements.  Show support locations, type of support, and weight on each support.  Indicate and certify field measurements.

D. Product Certificates:  Signed by manufacturers of switchgear certifying that the products furnished comply with requirements.

E. Qualification Data:  For firms and persons specified in "Quality Assurance" Article.

F. Field Test Reports:  Indicate and interpret test results for compliance with performance requirements.

G. Product Test Reports:  Indicate compliance of switchgear with requirements.

H. Maintenance Data:  For switchgear to include in the maintenance manuals specified in Division 1.

1.4 QUALITY ASSURANCE

A. Manufacturer Qualifications:  Engage a firm experienced in manufacturing switchgear similar to those indicated for this Project and with a record of successful in-service performance.

Delete paragraph and subparagraph below if not required at Project location.  Verify that Section title listed is correct for this Project's Specifications because Section title may have changed since this Section was updated.

B. Testing Agency Qualifications:  In addition to the requirements specified in Division 1 Section "Quality Control," an independent testing agency shall meet OSHA criteria for accreditation of testing laboratories, Title 29, Part 1907; or shall be a full-member company of the InterNational Electrical Testing Association.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies, to supervise on-site testing specified in Part 3.

C. Source Limitations:  Obtain switchgear through one source from a single manufacturer.

Retain paragraph below to allow Drawing details based on one manufacturer's product to establish requirements and still allow competition.  Revise below to identify specific proprietary system or indicate on Drawings.  Correlate with Division 1 requirements and verify that Section title listed is correct for this Project's Specifications because Section title may have changed since this Section was updated.

D. Product Options:  Drawings indicate size, profiles, and dimensional requirements of switchgear and are based on specific system indicated.  Other manufacturers' systems with equal performance characteristics may be considered.  Refer to Division 1 Section "Substitutions."

Delete nonapplicable standards below.

E. Comply with NFPA 70.

F. Comply with IEEE C2.

1.5 DELIVERY, STORAGE, AND HANDLING

Delete paragraph below if there are no likely obstacles to handling switchgear assemblies.

A. Deliver in shipping splits of lengths that can be moved past obstructions in delivery path as indicated.

B. Store so condensation will not form on or in switchgear.

C. Apply temporary heat where required to obtain suitable service conditions.

D. Handle switchgear using factory-installed lifting provisions.

1.6 PROJECT CONDITIONS

Delete paragraph below if no existing utilities.  Coordinate with requirements specified in Division 1 Section "Construction Facilities and Temporary Controls" for temporary utilities.

A. Existing Utilities:  Do not interrupt utilities serving facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary utility services according to requirements indicated:

Edit subparagraph below to suit Project.

1. Notify Architect not less than two days in advance of proposed utility interruptions.

2. Do not proceed with utility interruptions without Architect's written permission.

1.7 COORDINATION

A. Coordinate layout and installation of switchgear with other construction.

Delete paragraphs below if not required.  Verify that Section titles listed are correct for this Project's Specifications because Section titles may have changed since this Section was updated.

B. Coordinate size and location of concrete or mounting bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3 Section "Cast-in-Place Concrete."

C. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 7 Section "Roof Accessories."

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed, are packaged with protective covering for storage, and are identified with labels describing contents.

Revise subparagraphs below as required.  Replace percentage with a specific number of units and replace unit with an expanded description of each unit.

1. Spare Fuses:  Six, of each type and rating of fuse used.  Include spares for power fuses, potential transformer fuses, control power fuses, and fuses and fusible devices for fused circuit breakers.

2. Spare Indicating Lights:  Six, of each type installed.

3. Touchup Paint:  Three containers of paint matching enclosure finish, each 0.5 pint (250 mL).

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1. Metal-Enclosed Interrupter Switchgear:

a. ASEA Brown Boveri, Inc.

b. Kearney-National; Kearney Div.

c. S&C Electric Co.

d. Siemens Energy & Automation, Inc.

e. Square D Co.

f. Westinghouse Electric Corp.; Electric Components Div.

2. Metal-Clad Circuit-Breaker Switchgear:

a. ASEA Brown Boveri, Inc.

b. GE Electrical Distribution & Control.

c. Siemens Energy & Automation, Inc.

d. Square D Co.

e. Westinghouse Electric Corp.; Electric Components Div.

2.2 MANUFACTURED UNITS

A. Description:  Factory assembled and tested, and complying with IEEE C37.20.1.

Retain paragraph below if installation space for switchgear is severely limited; show maximum dimensions on Drawings.  Ensure equipment is available.

B. Product Selection for Restricted Space:  Comply with maximum dimensions indicated on Drawings.

Specify unusual service conditions in paragraph below.  If there is more than one switchgear lineup and unusual conditions do not apply to all, edit to clarify applicability of conditions.  See Editing Instruction No. 2 in the Evaluations.

C. Unusual Service Conditions:  Where indicated, provide switchgear assemblies designed for the following conditions:

Add description of unusual service conditions and specify features required to provide satisfactory service despite conditions.

2.3 RATINGS

Modify paragraph below to suit actual system type in which switchgear will be installed.

A. System Configuration:  Switchgear suitable for application in three-phase, 60-Hz, grounded-neutral system.

Select one of four subparagraphs below or, if actual voltage is different, delete all and specify actual nominal voltage.

1. System Voltage:  4.16 kV nominal; 4.76 kV maximum.

2. System Voltage:  7.2 kV nominal; 15 kV maximum.

3. System Voltage:  13.8 kV nominal; 15 kV maximum.

4. System Voltage:  34.5 kV nominal; 38 kV maximum.

2.4 METAL-ENCLOSED INTERRUPTER SWITCHGEAR

A. Comply with IEEE C37.20.3.

Specify fuses in "Power Fuses" Paragraph and indicate both available-source fault current and required fuse interrupting rating on Drawings.

B. Design Level of Available-Source Fault Current:  Integrated short-circuit rating consistent with value of fault current indicated.

C. Ratings:  Comply with standard ratings designated in IEEE C37.20.3 for the maximum-rated voltage specified.

Select one of three subparagraphs below;  delete if shown on Drawings.

1. Main-Bus Continuous:  600 A.

2. Main-Bus Continuous:  1200 A.

3. Main-Bus Continuous:  2000 A.

D. Interrupter Switches:  Stationary, gang operated, suitable for application to maximum short-circuit rating of integrated switchgear assembly.

1. Rating:  600-A continuous duty and load break.

Select subparagraph above or below.

2. Rating:  1200-A continuous duty and load break.

a. Duty-Cycle, Fault Closing:  25,000 asymmetrical amperes.

b. Duty-Cycle, Fault Closing:  40,000 asymmetrical amperes.

3. Switch Action:  No external arc and no significant quantities of ionized gas released into the enclosure.

4. Switch Construction:  Supported entirely by interior framework of structure, with copper switch blades and stored-energy operating mechanism.

5. Phase Barriers:  Full length of blades and fuses for each pole; designed for easy removal; allow visual inspection of switch components if barrier is in place.

6. Protective Shields:  Cover live components and terminals.

E. Fuses:  De-energized when switch is open.

F. Mechanical Interlock:  Prevents opening switch compartment door unless switch blades are open, and prevents closing switch if door is open.

G. Window:  Permits viewing switch-blade positions if door is closed.

H. Accessory Set:  Tools and miscellaneous items required for interrupter switchgear test, inspection, maintenance, and operation.  Include fuse-handling tool as recommended by switchgear manufacturer.

I. Power Fuses:  Comply with applicable requirements of NEMA SG 2 and the following:

1. Indicator:  Integral with each fuse and shows when it has blown.

2. Mounting:  Fuses are positively held in position with provision for easy removal and replacement from the front without special tools.

Select one of two subparagraphs below.

3. Current-Limiting Fuses:  Full-range, fast-replaceable, current-limiting type that will operate without explosive noise or expulsion of gas, vapor, or foreign matter from tube.

4. Expulsion Fuses:  Furnished in disconnect-type mountings and renewable with replacement fuse units.  Gases emitted on interruption controlled and silenced by chambers designed for that purpose.

Coordinate below with Drawings and provide rating consistent with available short-circuit capacity of system.

5. Interrupting Ratings of Fuses at Rated System Voltage:  As indicated.

2.5 METAL-CLAD CIRCUIT-BREAKER SWITCHGEAR

A. Comply with IEEE C37.20.2.

Select one of five paragraphs below.

B. Nominal Interrupting-Capacity Class:  250 MVA.

C. Nominal Interrupting-Capacity Class:  350 MVA.

D. Nominal Interrupting-Capacity Class:  500 MVA.

E. Nominal Interrupting-Capacity Class:  750 MVA.

F. Nominal Interrupting-Capacity Class:  1000 MVA.

G. Ratings:  Based on IEEE C37.04 and ANSI C37.06.

Select one of three subparagraphs below; delete if shown on Drawings.

1. Main-Bus Continuous:  1200 A.

2. Main-Bus Continuous:  2000 A.

3. Main-Bus Continuous:  3000 A.

Select one of two paragraphs below.  See Editing Instruction No. 3 in the Evaluations.

H. Vacuum Circuit Breakers:  Drawout mounted units using three individual, vacuum-sealed contact modules and including the following features:

1. Circuit-Breaker Design:  Operates at rated voltage to interrupt fault current within its rating within three cycles of trip initiation.  For systems with X/R ratio of 17 or less, the transient voltage during interruption does not exceed twice the rated line-to-ground voltage of the system.

2. Contact-Wear Indicator:  Readily accessible to field maintenance personnel.

3. Spare Auxiliary Contacts:  Six minimum.

I. Sulfur-Hexafluoride Circuit Breakers:  Drawout mounted units using three independently sealed, sulfur-hexafluoride interrupter modules.

1. Circuit-Breaker Design:  Operates at rated voltage to interrupt fault current within its rating within five cycles of trip initiation.  For systems with X/R ratio of 17 or less, the transient voltage during interruption does not exceed twice the rated line-to-ground voltage of the system.

2. Internal sulfur-hexafluoride pressure not to exceed 2.5 bar during normal operation.

3. Contact-Wear Indicator:  Readily accessible to field maintenance personnel.

4. Interchangeability:  Circuit breakers are interchangeable with vacuum circuit breakers of the same current and interrupting ratings.

5. Circuit-Breaker Features:  Include the following:

a. Spare Auxiliary Contacts:  Six minimum.

Delete or revise three subparagraphs below to suit Project.

b. Current Rating of Main Circuit Breaker:  2000 A.

c. Continuous Current Rating of Tie Circuit Breaker:  2000 A.

d. Continuous Current Rating of Feeder Circuit Breaker:  1200 A.

6. Operating Mechanism:  Electrically charged, mechanically and electrically trip-free, stored-energy operated.

a. Closing Speed of Moving Contacts:  Independent of both control and operator.

b. Design of Mechanism:  Permits manual charging of mechanism and slow closing of contacts for inspection or adjustment.

Select one of three subparagraphs below.  See Evaluations for options.

1) Control Power:  125-V, dc for closing and tripping.

2) Control Power:  48-V, dc for closing and tripping.

3) Control Power:  230-V, ac for closing; 230-V, dc for capacitor tripping.

c. Circuit-Breaker Tripping Provisions:  Shunt tripping available independent of overcurrent trip.

Delete items in paragraphs below if not required.

J. Accessory Set:  Tools and miscellaneous items required for circuit-breaker and switchgear test, inspection, maintenance, and operation.  Include extension rails, lifting device, and transport or dockable dolly or mobile lift, and all other items necessary to remove circuit breaker from housing and transport to remote location.  Include a racking handle to move circuit breaker manually between connected and disconnected positions and a secondary test coupler to permit testing of circuit breaker without removal from switchgear.  Include relay and meter test plugs.

Coordinate paragraph below with Drawings.

K. Low-dc-Voltage Alarm:  Monitors dc, control power voltage and indicates an alarm at a location shown on Drawings when voltage falls to an adjustable value indicative of impending battery failure.  Factory set at 80 percent of full-charge voltage.

Delete paragraph below if not required by serving utility Company or by medium-voltage maintenance and testing agency serving Project facility.  Paragraph and subparagraphs below are a brief synopsis of one utility's requirements.  Revise to suit Project.

L. Grounding and Test Device System:  Suitable for phasing out, testing, and grounding switchgear bus or feeder if device is installed in place of circuit breaker; includes the following:

1. Portable Grounding and Test Device:  Interchangeable with drawout, medium-voltage circuit breakers to provide interlocked electrical access to either bus or feeder; electrically operated.

2. System control cabinet permanently mounted near switchgear.

3. Portable Remote-Control Station:  For grounding and test device.

4. Control-Cabinet Coupler Cable:  Adequate length to connect device inserted in any switchgear cubicle and control cabinet.

5. Remote-Control Coupler Cable:  50-foot (15-m) cable length to connect control cabinet and portable remote-control station.

6. Permanent Control Power Wiring:  From control cabinet to power source.

7. Protective Cover:  Fabricated of heavy-duty plastic and fitted to device.

8. Approval of Grounding and Test Device System:  Obtain approval of final system design from power company and agency designated by Owner to handle future maintenance of medium-voltage switchgear.

Coordinate paragraph below with Drawings.

M. Circuit-Breaker Test Cabinet:  Separately mounted and containing push buttons for circuit-breaker closing and tripping, control relay, fuses, and secondary coupler with cable approximately 9 feet (3 m) long.  Include a set of secondary devices for operating circuit breaker if removed from switchgear and moved near test cabinet.  Include provision for storage of test and maintenance accessories in cabinet.

Delete below if not required.

N. Remote-Tripping Device:  Wall-mounted emergency control station to open circuit breakers, in a red, cast-metal box with break-glass operation.

2.6 FABRICATION

A. Indoor Enclosure:  Steel.

Retain paragraph above or below or both, and edit to suit Project.  Consider local experience and practice, especially for outdoor switchgear.

B. Outdoor Enclosure:  Galvanized steel, weatherproof construction; integral structural-steel base frame with factory-applied asphaltic undercoating; and each compartment equipped with the following features:

Revise wind speed below to suit local conditions.

1. Structural design and anchorage adequate to resist loads imposed by 125-mph (200-km/h) wind.

2. Space heater operating at one-half or less of rated voltage, sized to prevent condensation.

3. Louvers equipped with insect/rodent screen and filter and arranged to permit air circulation while excluding exterior dust and rodents.

Delete three subparagraphs below if weatherproof internal aisle construction is specified.

4. Hinged front door with padlocking provisions.

5. Interior light with switch.

6. Weatherproof duplex receptacle.

7. Common internal aisle of sufficient width to permit protective-device withdrawal, disassembly, and servicing in aisle.

8. Aisle access doors with outside padlocking provisions and interior panic latches.

9. Aisle space heaters operating at one-half or less of rated voltage, thermostatically controlled.

10. Vaporproof fluorescent aisle lights with low-temperature ballasts, controlled by wall switch at each entrance.

11. Duplex receptacles, a minimum of two, located in aisle.

Expand subparagraph below if forced ventilation rather than convection ventilation is required.

12. Aisle ventilation louvers equipped with insect/rodent screen and filter and arranged to permit air circulation while excluding exterior dust and rodents.

C. Finish:  Manufacturer's standard gray finish over a rust-inhibiting primer on phosphatizing-treated metal surfaces.

D. Bus Transition Unit:  Arranged to suit bus and adjacent units.

E. Incoming-Line Unit:  Arranged to suit incoming line.

F. Outgoing Feeder Units:  As indicated.

G. Auxiliary Compartments:  Arranged to house meters, relays, controls, and auxiliary equipment; isolated from medium-voltage components.

H. Key Interlocks:  Arranged to effect interlocking schemes indicated.

I. Provisions for Future Key Interlocks:  Mountings and hardware required for future installation of locks, where indicated.

2.7 COMPONENTS

Select one of three paragraphs below.

A. Main Bus:  Copper, silver plated at connection points.

B. Main Bus:  Copper, tin plated.

C. Main Bus:  Aluminum, tin plated.

D. Ground Bus:  Copper, silver, or tin plated; minimum size 1/4 by 2 inches (6 by 50 mm); full length of switchgear.

E. Bus Insulation:  Covered with flame-retardant insulation.

F. Instrument Transformers:  Comply with IEEE C57.13.

1. Potential Transformers:  Secondary voltage rating of 120 V and NEMA accuracy class of 0.3 with burdens of W, X, and Y.

Coordinate subparagraph below with Drawings.

2. Current Transformers:  Ratios as indicated; burden and accuracy class suitable for connected relays, meters, and instruments.

Delete paragraph below if conventional analog-meter installation is required.  See Editing Instruction No. 4 in the Evaluations.

G. Multifunction Digital-Metering Monitor:  UL-listed or -recognized, microprocessor-based unit suitable for three- or four-wire systems and with the following features:

1. Inputs from sensors or 5-A current-transformer secondaries, and potential terminals rated to 600 V.

2. Switch selectable digital display of the following:

a. Phase Currents, Each Phase:  Plus or minus 1 percent.

b. Phase-to-Phase Voltages, Three Phase:  Plus or minus 1 percent.

c. Phase-to-Neutral Voltages, Three Phase:  Plus or minus 1 percent.

d. Three-Phase Real Power:  Plus or minus 2 percent.

e. Three-Phase Reactive Power:  Plus or minus 2 percent.

f. Power Factor:  Plus or minus 2 percent.

g. Frequency:  Plus or minus 0.5 percent.

h. Integrated Demand, with Demand Interval Selectable from 5 to 60 Minutes:  Plus or minus 2 percent.

Delete subparagraph below if not required.

i. Accumulated energy, in megawatt hours (joules), plus or minus 2 percent; stored values unaffected by power outages for up to 72 hours.

3. Mounting:  Display and control unit flush or semiflush mounted in instrument compartment door.

Delete paragraph below if digital metering above is specified.

H. Analog Instruments:  Rectangular, 4-1/2-inch (115-mm) square, 1 percent accuracy, semiflush, with antiparallax 250-degree scale and external zero adjustment, complying with ANSI C39.1.

1. Voltmeters:  Cover an expanded scale range of normal voltage plus 10 percent.

Delete "phase-to-neutral" below for three-wire systems.

2. Voltmeter Selector Switch:  Rotary type with off position to provide readings of phase-to-phase and phase-to-neutral voltages.

3. Ammeters:  Cover an expanded scale range of bus rating plus 10 percent.

4. Ammeter Selector Switch:  Permits current reading in each phase and keeps current-transformer secondary circuits closed in off position.

5. Locate meter and selector switch on circuit-breaker compartment door for indicated feeder circuits only.

Revise demand interval and other characteristics in subparagraphs below to suit Project.

6. Watt-Hour Meters:  Flush or semiflush type, 5 A, 120 V, 3 phase, 3 wire; with 3 elements, 15-minute indicating demand register, and provision for testing and adding pulse initiation.

7. Recording Demand Meter:  Usable as totalizing relay or indicating and recording maximum demand meter with 15-minute interval.

a. Operation:  Meter counts and records a succession of pulses entering two channels.

b. Housing:  Drawout, back-connected case arranged for semiflush mounting.

Delete paragraph below unless relays not integral with circuit breakers or circuit-breaker trip units are required.  Specify relay functions and characteristics below or indicate on Drawings.

I. Relays:  Comply with IEEE C37.90, types and settings as indicated; with test blocks and plugs.

Delete paragraph below if system analysis shows arresters are not required at switchgear.  Show ratings of arresters on Drawings.

J. Surge Arresters:  Distribution class, metal-oxide-varistor type.  Comply with NEMA LA 1.

1. Install in cable termination compartments and connect in each phase of circuit.

2. Coordinate rating with circuit voltage.

Delete paragraph below if not required.  Coordinate with Drawings.

K. Provision for Future Devices:  Equip compartments with rails, mounting brackets, supports, necessary appurtenances, and bus connections.

Delete paragraph below except for installation in tropical environments.

L. Fungus Proofing:  Permanent fungicidal treatment for switchgear interior, including instruments and instrument transformers.

M. Control Power Supply:  DC battery system.

Select paragraph above or below.  If retaining above, retain "Control Battery System" Article below.

N. Control Power Supply:  Control power transformer supplies 120-V control circuits through secondary disconnect devices.  Include the following features:

1. Dry-type transformers, in separate compartments for units larger than 3 kVA, including primary and secondary fuses.

Retain subparagraph below for electrically interlocked main and tie circuit breakers.

2. Two control power transformers in separate compartments with necessary interlocking relays; each transformer connected to line side of associated main circuit breaker.

Delete one of two subparagraphs below.

a. Secondaries connected through a relay or relays to control bus to effect an automatic transfer scheme.

b. Secondaries connected through an internal automatic transfer switch to switchgear control power bus.

3. Control Power Fuses:  Primary and secondary fuses provide current-limiting and overload protection.

O. Control Wiring:  Factory installed, complete with bundling, lacing, and protection; and complying with the following:

1. Flexible conductors for No. 8 AWG and smaller, for conductors across hinges, and for conductors for interconnections between shipping units.

2. Conductors sized according to NFPA 70 for the duty required.

2.8 CONTROL BATTERY SYSTEM

Delete this Article if dc, control power source is not required.  Revise if battery other than lead-calcium type below is specified.

Coordinate paragraph below with Drawings or, preferably, revise to specify number of cells and required minimum ampere-hour capacity of battery.

A. System Requirements:  Battery has number of cells and ampere-hour capacity and rating as indicated, based on an initial specific gravity of 1.210 at 25 deg C with electrolyte at normal level and minimum ambient temperature of 13 deg C.  Cycle battery before shipment to guarantee rated capacity on installation.  Arrange battery to operate ungrounded.

B. Battery:  Lead-calcium type in sealed, clear plastic or glass containers, complete with electrolyte, fully charged, and arranged for shipment with electrolyte in cells.  Each container weighs not more than 70 lb (32 kg) and contains not more than three cells.  Batteries are suitable for service at an ambient temperature ranging from minus 18 to 25 deg C.  Current output does not vary more than 0.8 percent for each degree below 25 deg C down to minus 8 deg C.

Coordinate two paragraphs below with Drawings.

C. Rack:  Provide a two-step rack that fits available space indicated.  Batteries are provided with necessary electrical connections between cells and between rows of cells and include two flexible connectors with bolted-type terminals for output leads.

D. Accessories:  Include the following:

1. Thermometers with specific-gravity correction scales.

2. Hydrometer syringes.

3. Set of socket wrenches and other tools required for battery maintenance.

4. Wall-mounted, nonmetallic storage rack fitted to store above items.

5. Set of cell numerals.

E. Charger:  Static-type silicon rectifier equipped with automatic regulation and provision for manual and automatic adjustment of the charging rate.  Unit automatically maintains output voltage within 0.5 percent from no load to rated charger output current, with ac input-voltage variation of plus or minus 10 percent and input-frequency variation of plus or minus 3 Hz.  Other features of charger include the following:

1. DC ammeter.

2. DC Voltmeter:  Maximum error of 5 percent at full-charge voltage; operates with toggle switch to select between battery and charger voltages.

3. Ground Indication:  Two appropriately labeled lights to indicate circuit ground, connected in series between negative and positive terminals, with midpoint junction connected to ground by normally open push-button contact.

4. Capacity:  Sufficient to supply steady load, float-charge battery between 2.20 and 2.25 V per cell, and equalizing charge at 2.33 V per cell.

5. Charging-Rate Switch:  Manually operated switch provides for transferring to higher charging rate.  Charger operates automatically after switch operation until manually reset.

6. AC power supply is 120 V, 60 Hz, subject to plus or minus 10 percent variation in voltage and plus or minus 3-Hz variation in frequency.  After loss of ac power supply for any interval, charger automatically resumes charging battery.  Charger regulates rate of charge to prevent damage due to overload and to prevent fuses or circuit breakers from opening.

7. Protective Feature:  Current-limiting device or circuit, which limits output current to rating of charger but does not disconnect charger from either battery or ac supply; to protect charger from damage due to overload, including short circuit on output terminals.

8. Electrical Filtering:  Reduces charger's audible noise to less than 26 dB.

2.9 IDENTIFICATION

A. Materials:  Refer to Division 16 Section "Electrical Identification."  Identify units, devices, controls, and wiring.

Retain paragraph above or below.  Verify that Section titles listed are correct for this Project's Specifications because Section titles may have changed since this Section was updated.

B. Materials:  Refer to Division 16 Section "Basic Electrical Materials and Methods."  Identify units, devices, controls, and wiring.

Delete paragraph below if not required.

C. Mimic Bus:  Continuous mimic bus applied to front of switchgear, arranged in single-line diagram format, using symbols and lettered designations consistent with approved final mimic-bus diagram.

1. Mimic-bus segments coordinated with devices in switchgear sections to which applied, to produce a concise visual presentation of principal switchgear components and connections.

2. Medium:  Painted graphics, as approved.

3. Color:  Contrasting with factory-finish background, selected by Architect.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Locations and Layout:  Exact locations and physical layout of equipment and components may be varied as required to suit manufacturer's design and as approved, provided the required functions and operations are accomplished; follow the identification of the units indicated on Drawings exactly to ease checking and building maintenance procedures.

Delete paragraph below if not required and provide alternate anchoring.  Coordinate with Drawings.  Add requirements for seismic restraints if applicable.

B. Anchor each switchgear assembly to at least two 4-inch (100-mm), channel-iron floor sills arranged according to the manufacturer's written recommendations; attach by tack welding or bolting.

1. Sills:  Select to suit switchgear; level and grout flush into floor or concrete or mounting base.

Delete subparagraph below if not required.  Coordinate with Drawings.  Verify that Section title listed is correct for this Project's Specifications because Section title may have changed since this Section was updated.

2. Concrete Bases:  4 inches (100 mm) high, reinforced, with chamfered edges.  Extend base no more than 2 inches (50 mm) in all directions beyond the maximum dimensions of the switchgear, unless otherwise indicated.  Comply with Division 3 Section "Cast-in-Place Concrete."

C. Temporary Lifting Provisions:  Remove temporary lifting eyes, channels, brackets, and temporary blocking of moving parts from switchgear units and components.

3.2 IDENTIFICATION

A. Identify field-installed wiring and components and provide warning signs as specified in Division 16 Section "Electrical Identification."

Retain paragraph above or below.  Verify that Section titles listed are correct for this Project's Specifications because Section titles may have changed since this Section was updated.

B. Identify field-installed wiring and components and provide warning signs as specified in Division 16 Section "Basic Electrical Materials and Methods."

C. Diagram and Instructions:  Frame under clear acrylic plastic on the front of switchgear.

1. Operating Instructions:  Printed basic instructions for switchgear, including control and key-interlock sequences and emergency procedures.

2. Storage for Manual:  Include a rack or holder, near the operating instructions, for a copy of the maintenance manual.

3. System Power Riser Diagrams:  Depict power sources, feeders, distribution components, and major loads.

3.3 CONNECTIONS

A. Connect switchgear ground bus to common building ground indicated on Drawings.

B. Tighten bus joint, connector, and terminal bolts according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.4 FIELD QUALITY CONTROL

Retain paragraph below unless qualified services are available outside manufacturer's service group.

A. Manufacturer's Field Services:  Engage a factory-authorized service representative to inspect field-assembled components, installation, and connection of switchgear; and to pretest and adjust switchgear components.  Report results in writing.

B. Testing Agency:  Owner will engage a qualified independent testing agency to perform field quality-control testing.

Delete paragraph above or below.  Retain below if testing agency services are in this Contract.  Delete both if Contractor will perform field quality-control testing.

C. Testing Agency:  Engage a qualified independent testing agency to perform field quality-control testing.

D. Testing:  After installing switchgear and after electrical circuitry has been energized, demonstrate product capability and compliance with requirements.

1. Procedures:  Perform inspections and tests specified below.  Report values that do not meet manufacturer's written recommendations.  Certify compliance with test parameters.

2. Switchgear:  Perform inspections and tests stated in NETA ATS, Section 7.1.

3. Circuit Breakers:  Perform inspections and tests stated in NETA ATS, Section 7.6.

4. Protective Relays:  Perform inspections and tests stated in NETA ATS, Section 7.9.

5. Instrument Transformers:  Perform inspections and tests stated in NETA ATS, Section 7.10.

6. Metering and Instrumentation:  Perform inspections and tests stated in NETA ATS, Section 7.11.

7. Ground-Fault Systems:  Perform inspections and tests stated in NETA ATS, Section 7.14.

8. Battery Systems:  Perform inspections and tests stated in NETA ATS, Section 7.18.

9. Surge Arresters:  Perform inspections and tests stated in NETA ATS, Section 7.19.

10. Capacitors:  Perform inspections and tests stated in NETA ATS, Section 7.20.

E. Remove and replace malfunctioning units with new units and retest.

F. Infrared Scanning:  After Substantial Completion, but not more than two months after Final Acceptance, perform an infrared scan of switchgear assembly.  Make bus joints and connections accessible to a portable scanner and perform scanning during a period of normal working load as advised by Owner.

1. Follow-up Infrared Scanning:  Perform one additional follow-up infrared scan at same locations as before, 11 months after date of Substantial Completion.

2. Instrument:  Use an infrared scanning device designed to measure temperature or detect significant deviations from normal values.  Provide calibration record for scanning device used for electrical distribution equipment.

3. Record of Infrared Scanning:  Prepare a certified report identifying all connections checked and describing results of scanning.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

3.5 ADJUSTING

A. Protective-Relay Settings:  Verify that settings shown on Drawings are appropriate for final system configuration and parameters.  Where discrepancies are found, recommend final relay settings for approval before making final adjustments.

Select paragraph above or below if Contractor is responsible for verifying final settings and sizes.

B. Fuse Characteristics:  Verify that fuse size and types shown on Drawings are appropriate for final system configuration and parameters.  Where discrepancies are found, recommend fuse selection for approval before making final adjustments.

3.6 CLEANING

A. Inspect interior and exterior of installed switchgear.  Remove paint splatters and other spots, dirt, and debris.  Touch up scratches and mars of finish to match original finish.

3.7 PROTECTION

A. Temporary Heating:  Apply temporary heat to switchgear, according to manufacturer's written recommendations, throughout periods when switchgear environment is not controlled for temperature and humidity within manufacturer's stipulated service conditions.

3.8 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel in the following:

1. Train Owner's maintenance personnel on procedures and schedules related to startup and shutdown, troubleshooting, servicing, and preventive maintenance.

2. Review data in the maintenance manuals.  Refer to Division 1 Section "Contract Closeout."

Delete subparagraph above or below depending on which Section is retained in Division 1.  Verify that Section titles listed are correct for this Project's Specifications because Section titles may have changed since this Section was updated.

3. Review data in the maintenance manuals.  Refer to Division 1 Section "Operation and Maintenance Data."

4. Schedule training with Owner with at least seven days' advance notice.

END OF SECTION 16341

MEDIUM-VOLTAGE SWITCHGEAR
16341 - 1

