Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16410 - ENCLOSED SWITCHES AND CIRCUIT BREAKERS

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes individually mounted enclosed switches and circuit breakers, rated 600 V and less, used for disconnecting and protection functions.

B. See Division 16 Section "Fuses" for fuses for fusible disconnect switches.

1.2 SUBMITTALS

A. Product Data:  For each type of switch and circuit breaker indicated.

B. Shop Drawings:  Include wiring diagrams for shunt-tripped circuit breakers.

C. Field quality-control test reports.

D. Operation and maintenance data.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Source Limitations:  Obtain switches and circuit breakers through one source from a single manufacturer.

C. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Eaton Corp.; Cutler-Hammer Products.

2. General Electric Co.; Electrical Distribution & Control Division.

3. Siemens Energy & Automation, Inc.

4. Square D Co.

5. <Insert manufacturer.>

2.2 ENCLOSED SWITCHES

In two paragraphs below, consider general-duty (Type GD) switches for light-commercial applications, 240 V or less; otherwise, select heavy duty (Type HD).  See Editing Instruction No. 2 in the Evaluations.

A. Enclosed, Nonfusible Switch:  NEMA KS 1, Type  [GD] [HD], with lockable handle, interlocked with cover.

Edit below to indicate Project requirement for bolted-pressure contact switch, and high-pressure butt contact switch, or use Division 16 Section "Fused Power Circuit Devices" to specify these switches.

B. Enclosed, Fusible Switch, 800 A and Smaller:  NEMA KS 1, Type  [GD] [HD], with clips to accommodate specified fuses, and lockable handle, interlocked with cover.

2.3 ENCLOSED CIRCUIT BREAKERS

A. Molded-Case Circuit Breaker:  NEMA AB 1, with interrupting capacity to meet available fault currents.

1. Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

2. Adjustable Instantaneous-Trip Circuit Breakers:  Magnetic trip element with front-mounted, field-adjustable trip setting.

3. Current-Limiting Circuit Breakers:  Frame sizes 400 A and smaller; let-through ratings less than NEMA FU 1, RK-5.

4. GFCI Circuit Breakers:  Single- and two-pole configurations with [5] [30]-mA trip sensitivity.

B. Molded-Case Circuit-Breaker Features and Accessories:  Standard frame sizes, trip ratings, and number of poles.

1. Lugs:  Suitable for number, size, trip ratings, and material of conductors.

2. Application Listing:  Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

3. Ground-Fault Protection:  [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

4. Shunt Trip:  120-V trip coil energized from separate circuit, set to trip at [55] [75] percent of rated voltage.

2.4 ENCLOSURES

A. Listed for environmental conditions of installed locations, including:

Delete nonapplicable subparagraphs below.  Edit to suit Project.  Coordinate with Drawings.  See the Evaluations and Editing Instruction No. 2 in the Evaluations for discussion of enclosures.

1. Outdoor Locations:  NEMA 250, Type 3R.

2. Food Service Areas:  NEMA 250, Type 4X, stainless steel.

3. Other Wet or Damp Indoor Locations:  NEMA 250, Type 4.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Temporary Provisions:  Remove temporary lifting provisions and blocking of moving parts.

B. Identify components; provide warning signs as specified in Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]."

3.2 FIELD QUALITY CONTROL

A. Testing:  After installing disconnect switches and circuit breakers and after electrical circuits have been energized, demonstrate product capability and compliance with requirements.

B. Inspections and Tests for Switches and Circuit Breakers:  Make internal and external inspections and perform tests, including the following:

1. Inspect for freedom from physical damage, proper unit rating, mechanical condition, enclosure integrity, cover operation, unit anchorage, clearances, and tightness of electrical connections.  If a loose electrical connection is observed on any unit, check each electrical connection for each switch and circuit breaker with a torque wrench for compliance with manufacturer's torquing instructions.

2. Test insulation resistance of each pole, phase-to-phase, and phase-to-ground, following manufacturer's written instructions.  Test insulation resistance of shunt trip circuits.  Use 500-V minimum test voltage for units and circuits rated up to 250 V, 1000-V minimum test voltage for units rated more than 250 V.  Measured insulation resistance must be 25 megohms, minimum, for switches rated up to 250 V, and 100 megohms, minimum, for switches rated more than 250 V.

3. Test cover and other interlocks and interlock release devices for proper operation.

C. Additional Inspections and Tests for Switches:  Include the following:

1. Inspect for proper rating and fuse provisions.

2. Check adequacy and integrity of fuseholders by removing and installing fuses.

3. Check integrity of phase barriers.

4. Inspect blade alignment visually while operating switch to observe adequacy of blade pressure.

D. Additional Inspections and Tests for Circuit Breakers:  Include the following:

1. Inspect for proper frame, trip, and fault current interrupting rating.

2. Test shunt trip devices, circuits, and actuating components for proper operation.

E. Correct defective and malfunctioning units on-site, where possible, and reinspect and retest to demonstrate compliance; otherwise, remove and replace with new units and retest.

END OF SECTION 16410

ENCLOSED SWITCHES AND CIRCUIT BREAKERS
16410 - 1

