Copyright 1999 AIA
MASTERSPEC
3/99


Copyright 1999, The American Institute of Architects (AIA)

SECTION 16430 - SWITCHGEAR

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes metal-enclosed, low-voltage, power circuit-breaker switchgear rated 1000 V and less for use in ac systems.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

Retain subparagraph below if Project includes requirements for seismic controls.

1. Division 16 Section "Seismic Controls for Electrical Work" for mounting and anchoring switchgear.

Retain subparagraph below if Project includes requirements for electrical power monitoring and control.

2. Division 16 Section "Electrical Power Monitoring and Control" for interfacing communication and metering requirements.

Retain below if fuses are required for control-power transformers, potential transformers, or similar equipment.

3. Division 16 Section "Fuses" for fuses and spare-fuse cabinets.

1.3 SUBMITTALS

A. Product Data:  For each type of switchgear, circuit breaker, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes.

B. Shop Drawings:  For each type of switchgear and related equipment.

1. Dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment.  Show tabulations of installed devices, equipment features, and ratings.  Include the following:

a. Enclosure types and details.

b. Nameplate legends.

c. Bus configuration with size and number of conductors in each bus run, including phase, neutral, and ground conductors of main and branch buses.

d. Current rating of buses.

e. Short-time and short-circuit current rating of switchgear assembly.

f. Mimic-bus diagram.

Delete first three subparagraphs below if not required.

g. Utility company's metering provisions with indication of approval by utility company.

Delete first subparagraph below if series rating of overcurrent protective devices is not used.

h. UL listing for series rating of installed devices.

i. Features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.

2. Wiring Diagrams:  Diagram power, signal, and control wiring and differentiate between manufacturer-installed and field-installed wiring.

C. Coordination Drawings:  Floor plans showing dimensioned layout, required working clearances, and required area above and around switchgear where pipe and ducts are prohibited.  Show switchgear layout and relationships between components and adjacent structural and mechanical elements.  Show support locations, type of support, and weight on each support.  Indicate field measurements.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 16 Section "Seismic Controls for Electrical Work."

D. Manufacturer Seismic Qualification Certification:  Submit certification that switchgear, overcurrent protective devices, accessories, and components will withstand seismic forces defined in Division 16 Section "Seismic Controls for Electrical Work."  Include the following:

1. Basis of Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

E. Samples:  Representative portion of mimic bus with specified finish.  Manufacturer's color charts showing colors available for mimic bus.

Delete first paragraph below if independent testing agency is not used.

F. Qualification Data:  For firms and persons specified in "Quality Assurance" Article.

G. Field Test Reports:  Submit written test reports and include the following:

1. Test procedures used.

2. Test results that comply with requirements.

3. Results of failed tests and corrective action taken to achieve test results that comply with requirements.

H. Manufacturer's field service report.

I. Updated mimic-bus diagram reflecting field changes after final switchgear load connections have been made, for record.

J. Maintenance Data:  For switchgear and components to include in maintenance manuals specified in Division 1.  In addition to requirements specified in Division 1 Section "Closeout Procedures," include the following:

1. Routine maintenance requirements for switchgear and all installed components.

2. Manufacturer's written instructions for testing and adjusting overcurrent protective devices.

3. Time-current curves, including selectable ranges for each type of overcurrent protective device.

1.4 QUALITY ASSURANCE

Retain first paragraph and subparagraph below if Contractor or manufacturer selects testing agency.

A. Testing Agency Qualifications:  Testing agency that is a member company of the InterNational Electrical Testing Association and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

B. Source Limitations:  Obtain switchgear through one source from a single manufacturer.

Retain paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Revise to identify specific proprietary system or indicate on Drawings.  Correlate with Division 1 requirements.

C. Product Options:  Drawings indicate size, profiles, and dimensional requirements of switchgear and are based on the specific system indicated.  Other manufacturers' products complying with requirements may be considered.  Refer to Division 1 Section "Product Requirements."

Delete first paragraph below if labeling of switchgear is not required.  See Editing Instruction No. 2 in the Evaluations.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E. Comply with NFPA 70.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Deliver switchgear in sections of lengths that can be moved past obstructions in delivery path.

Delete one of two paragraphs below or edit to suit Project.

B. Store switchgear indoors in clean dry space with uniform temperature to prevent condensation.  Protect switchgear from exposure to dirt, fumes, water, corrosive substances, and physical damage.

C. If stored in areas subjected to weather, cover switchgear to provide protection from weather, dirt, dust, corrosive substances, and physical damage.  Remove loose packing and flammable materials from inside switchgear; install electric heating (250 W per section) to prevent condensation.

1.6 PROJECT CONDITIONS

Revise paragraph below to describe specific requirements for moving switchgear into place.  Where appropriate, indicate alterations to existing facilities that may be required to accommodate an indicated delivery path.  Coordinate with Drawings.

A. Installation Pathway:  Remove and replace building components and structures to provide pathway for moving switchgear into place.

Delete paragraph and subparagraphs below if no existing utilities.  Coordinate with requirements specified in Division 1 Section "Temporary Facilities and Controls" for temporary utilities.

B. Existing Utilities:  Do not interrupt utilities serving facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary utility services according to requirements indicated:

Edit first subparagraph below to suit Project.

1. Notify Architect not less than seven days in advance of proposed utility interruptions.  Identify extent and duration of utility interruptions.

2. Indicate method of providing temporary utilities.

3. Do not proceed with utility interruptions without Architect's written permission.

Retain paragraph below if installation space for switchgear is limited; show maximum dimensions on Drawings.

C. Product Selection for Restricted Space:  Drawings indicate maximum dimensions for switchgear, including clearances between switchgear, and adjacent surfaces and other items.  Comply with indicated maximum dimensions.

Specify unusual environmental or service conditions here.  See Editing Instruction No. 3 in the Evaluations.  Otherwise, indicate typical environmental conditions as follows:  For switchgear installed outdoors, indicate minimum ambient temperature and expected humidity range.

D. Environmental Limitations:  Rate equipment for continuous operation under the following conditions, unless otherwise indicated:

1. Ambient Temperature:  Not exceeding 40 deg C.

2. Altitude:  Not exceeding 6600 feet (2000 m).

3. <Insert unusual service conditions.>

1.7 COORDINATION

Edit first paragraph below to delete or add types of construction that penetrate or are supported by ceilings.

A. Coordinate layout and installation of switchgear and components with other construction that penetrates ceilings or is supported by them, including conduit, piping, equipment, and adjacent surfaces.  Maintain required clearances for workspace and equipment access doors and panels.

B. Coordinate size and location of concrete bases.

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

Revise paragraph and subparagraphs below to suit Project.  Coordinate with Division 16 Section "Fuses" for quantities of spare fuses to be provided.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Fuses:  [Six] <Insert number> of each type and rating used.  Include spares for potential transformer fuses, control power fuses, and fuses and fusible devices for fused circuit breakers.

2. Indicating Lights:  [Six] <Insert number> of each type installed.

3. Touchup Paint:  [Three] <Insert number> containers of paint matching enclosure finish, each 0.5 pint (250 mL).

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1. ABB Power T&D Co., Inc.; Distribution Systems Div.

2. Cutler-Hammer, Inc.

3. GE Electrical Distribution & Control.

4. Siemens Energy & Automation, Inc.

5. Square D Co./Groupe Schneider NA.

2.2 RATINGS

Delete this Article if ratings are indicated on Drawings.  Drawings are generally the preferred location for this data.

Select one system voltage from paragraph below.

A. Nominal System Voltage:  [480 V, 3] [480/277 V, 4] [240 V, 3] [208/120 V, 4] wire, 60 Hz.

Select one of four ratings in paragraph below and edit for actual rating.  Other standard bus ratings are available.  IEEE C37.20.1 lists main-bus ratings only through 4000 A, but some manufacturers will provide bus ratings through 5000 A.  However, circuit breakers are available only through 4000 A.

B. Main-Bus Continuous:  [4000] [3200] [2000] [1600]  A.

C. Short-Time and Short-Circuit Current:  Match rating of highest-rated circuit breaker in switchgear assembly.

2.3 FABRICATION

A. Factory assembled and tested and complying with IEEE C37.20.1.

B. Indoor Enclosure Material:  Steel.

Retain paragraph above or below or both, and edit to suit Project.  See Editing Instruction No. 4 in the Evaluations.

C. Outdoor Enclosure Material:  Galvanized steel.

D. Outdoor Enclosure Fabrication Requirements:  Weatherproof; integral structural-steel base frame with factory-applied asphaltic undercoating; and each compartment equipped with the following features:

Revise wind speed below to suit local conditions.

1. Structural design and anchorage adequate to resist loads imposed by 125-mph (200-km/h) wind.

2. Space heater operating at one-half or less of rated voltage, sized to prevent condensation.

3. Louvers equipped with insect and rodent screen and filter and arranged to permit air circulation while excluding insects, rodents, and exterior dust.

Delete first three subparagraphs below if weatherproof internal aisle construction is specified.

4. Hinged front door with padlocking provisions.

5. Interior light with switch.

6. Weatherproof duplex receptacle.

7. Common internal aisle of sufficient width to permit protective-device withdrawal, disassembly, and servicing in aisle.

8. Aisle access doors with outside padlocking provisions and interior panic latches.

9. Aisle space heaters operating at one-half or less of rated voltage, thermostatically controlled.

10. Vaporproof fluorescent aisle lights with low-temperature ballasts, controlled by wall switch at each entrance.

11. Duplex receptacles, a minimum of two, located in aisle.

Expand subparagraph below if forced ventilation rather than convection ventilation is required.

12. Aisle ventilation louvers equipped with insect and rodent screen and filter and arranged to permit air circulation while excluding insects, rodents, and exterior dust.

E. Finish:  IEEE C37.20.1, manufacturer's standard gray finish over a rust-inhibiting primer on phosphatizing-treated metal surfaces.

F. Section barriers between main and tie circuit-breaker compartments shall be extended to rear of section.

G. Bus isolation barriers shall be arranged to isolate line bus from load bus at each main and tie circuit breaker.

H. Circuit-breaker compartments shall be equipped to house drawout-type circuit breakers and shall be fitted with hinged outer doors.

I. Fabricate enclosure with removable, hinged, rear cover panels, secured by captive thumbscrews, to allow access to rear interior of switchgear.

J. Auxiliary Compartments:  Match and align with basic switchgear assembly.  Include the following:

Revise subparagraphs below to suit Project.

1. Utility metering compartment that complies with utility company requirements.

Coordinate first subparagraph below with Drawings.  Pull section is not usually required in low-voltage power switchgear.  Space available for incoming lines may be influenced by metering provisions and main circuit-breaker connections.  Edit to suit Project.

2. Bus transition sections.

3. Incoming-line pull sections.

4. Hinged front panels for access to metering, accessory, and blank compartments.

5. Pull box on top of switchgear for extra room for pulling cable, with removable top, front, and side covers and ventilation provisions adequate to maintain air temperature in pull box within same limits as switchgear.

Delete first subparagraph below if top-mounted, circuit-breaker removal mechanism is not used.

a. Set pull box back from front to clear circuit-breaker lifting mechanism.

b. Bottom:  Insulating, fire-resistant material with separate holes for cable drops into switchgear.

c. Cable Supports:  Arranged to ease cabling and adequate to support cables indicated, including those for future installation.

Coordinate paragraph and subparagraphs below with Drawings.

K. Bus bars connect between vertical sections and between compartments.  Cable connections are not permitted.

1. Main Phase Bus:  Uniform capacity the entire length of assembly.

Select one of two neutral bus ratings from subparagraph below.  See Editing Instruction No. 7 in the Evaluations.

2. Neutral Bus:  [50] [100] percent of phase-bus ampacity, except as indicated.  Equip bus with pressure-connector terminations for outgoing circuit neutral conductors.  Include braces for neutral-bus extensions for busway feeders.

Retain subparagraph below if switchgear assembly includes spare circuit breakers and spaces for future circuit breakers.  See Editing Instruction No. 6 in the Evaluations.

3. Vertical Section Bus Size:  Comply with IEEE C37.20.1, including allowance for spare circuit breakers and spaces for future circuit breakers.

Select one of first three subparagraphs below for main-bus material, or delete all and make selection Contractor's option.

4. Phase- and Neutral-Bus Material:  Hard-drawn copper of 98 percent minimum conductivity, with copper feeder circuit-breaker line connections.

5. Phase- and Neutral-Bus Material:  Silver- or tin-plated, high-strength, electrical-grade aluminum alloy, with copper or tin-plated aluminum circuit-breaker line connections.

6. Phase- and Neutral-Bus Material:  Hard-drawn copper of 98 percent minimum conductivity or tin-plated, high-strength, electrical-grade aluminum alloy.

7. Use silver-plated copper or tin-plated aluminum for connecting circuit-breaker line to aluminum bus.

Retain subparagraph above or below as required by bus-material specification.

8. Use copper for connecting circuit-breaker line to copper bus.

9. Contact Surfaces of Buses:  Silver plated.

10. Feeder Circuit-Breaker Load Terminals:  Silver-plated copper bus extensions equipped with pressure connectors for outgoing circuit conductors.

11. Ground Bus:  Hard-drawn copper of 98 percent minimum conductivity, with pressure connector for feeder and branch-circuit ground conductors, minimum size 1/4 by 2 inches (6 by 50 mm).

12. Supports and Bracing for Buses:  Adequate strength for indicated short-circuit currents.

13. Neutral bus equipped with pressure-connector terminations for outgoing circuit neutral conductors.  Neutral-bus extensions for busway feeders are braced.

Retain first subparagraph below for switchgear with main service disconnect switches.  Edit to suit Project.  Coordinate with Drawings.

14. Neutral Disconnect Link:  Bolted, uninsulated, 1/4-by-2-inch (6-by-50-mm) copper bus, arranged to connect neutral bus to ground bus.

15. Provide for future extensions from either end of main phase, neutral, and ground bus by means of predrilled bolt-holes and connecting links.

IEEE and UL standards may require air insulation only.  Retain subparagraph and associated subparagraphs below if insulated bus is required.

16. Bus-Bar Insulation:  Individual bus bars wrapped with factory-applied, flame-retardant tape or spray-applied, flame-retardant insulation.

a. Sprayed Insulation Thickness:  3 mils (0.08 mm), minimum.

b. Bolted Bus Joints:  Insulate with secure joint covers that can easily be removed and reinstalled.

2.4 COMPONENTS

A. Instrument Transformers:  Comply with IEEE C57.13.

1. Potential Transformers:  Secondary-voltage rating of 120 V and NEMA accuracy class of 0.3 with burdens of W, X, and Y.

Coordinate subparagraph below with Drawings.

2. Current Transformers:  Ratios as indicated; burden and accuracy class suitable for connected relays, meters, and instruments.

Delete paragraph and subparagraphs below if conventional analog-meter installation is required.  See Editing Instruction No. 5 in the Evaluations.

B. Multifunction Digital-Metering Monitor:  UL-listed or -recognized, microprocessor-based unit suitable for three- or four-wire systems and with the following features:

1. Inputs from sensors or 5-A current-transformer secondaries, and potential terminals rated to 600 V.

2. Switch-selectable digital display of the following:

a. Phase Currents, Each Phase:  Plus or minus 1 percent.

b. Phase-to-Phase Voltages, Three Phase:  Plus or minus 1 percent.

c. Phase-to-Neutral Voltages, Three Phase:  Plus or minus 1 percent.

d. Three-Phase Real Power:  Plus or minus 2 percent.

e. Three-Phase Reactive Power:  Plus or minus 2 percent.

f. Power Factor:  Plus or minus 2 percent.

g. Frequency:  Plus or minus 0.5 percent.

h. Integrated Demand, with Demand Interval Selectable from 5 to 60 Minutes:  Plus or minus 2 percent.

Delete subparagraph below if not required.

i. Accumulated energy, in megawatt hours (joules), plus or minus 2 percent; stored values unaffected by power outages for up to 72 hours.

3. Mounting:  Display and control unit flush or semiflush mounted in instrument compartment door.

Delete paragraph and subparagraphs below if digital metering above is specified.

C. Analog Instruments:  Rectangular, 4-1/2-inch (115-mm) square, accurate within 1 percent, semiflush, with antiparallax 250-degree scale and external zero adjustment, complying with ANSI C39.1.

1. Voltmeters:  Cover an expanded scale range of normal voltage plus 10 percent.

Delete "phase-to-neutral" in first subparagraph below for three-wire systems.

2. Voltmeter Selector Switch:  Rotary type with off position to provide readings of phase-to-phase and phase-to-neutral voltages.

3. Ammeters:  Cover an expanded scale range of bus rating plus 10 percent.

4. Ammeter Selector Switch:  Permits current reading in each phase and keeps current-transformer secondary circuits closed in off position.

5. Locate meter and selector switch on circuit-breaker compartment door for indicated feeder circuits only.

Revise demand interval and other characteristics in subparagraphs and associated subparagraphs below to suit Project.

6. Watt-Hour Meters:  Flush or semiflush type, 5 A, 120 V, 3 phase, 3 wire; with 3 elements, 15-minute indicating demand register, and provision for testing and adding pulse initiation.

7. Recording Demand Meter:  Usable as totalizing relay or indicating and recording maximum demand meter with 15-minute interval.

a. Operation:  Meter counts and records a succession of pulses entering two channels.

b. Housing:  Drawout, back-connected case arranged for semiflush mounting.

Delete paragraph below unless relays not integral with circuit breakers or circuit-breaker trip units are required.  Specify relay functions and characteristics below or indicate on Drawings.

D. Relays:  Comply with IEEE C37.90, types and settings as indicated; with test blocks and plugs.

Delete paragraph and subparagraphs below if system analysis shows arresters are not required at switchgear.  Show ratings of arresters on Drawings.

E. Surge Arresters:  Distribution class, metal-oxide-varistor type.  Comply with IEEE C62.11 and NEMA LA 1.

1. Install in cable termination compartments and connect in each phase of circuit.

2. Coordinate rating with circuit voltage.

Delete paragraph below if not required.  Coordinate with Drawings.

F. Provision for Future Devices:  Equip compartments with rails, mounting brackets, supports, necessary appurtenances, and bus connections.

Delete paragraph below except for installation in tropical environments.

G. Fungus Proofing:  Permanent fungicidal treatment for switchgear interior, including instruments and instrument transformers.

Edit paragraph and subparagraphs below to accommodate special needs, such as dc control, battery, or uninterruptible power supply for control.

H. Control Power Supply:  Control power transformer supplying 120-V control circuits through secondary disconnect devices.  Include the following features:

1. Dry-type transformers, in separate compartments for units larger than 3 kVA, including primary and secondary fuses.

Retain subparagraph below for electrically interlocked main and tie circuit breakers.

2. Two control power transformers in separate compartments with necessary interlocking relays; each transformer connected to line side of associated main circuit breaker.

Delete one of two subparagraphs below.

a. Secondary windings connected through a relay or relays to control bus to effect an automatic transfer scheme.

b. Secondary windings connected through an internal automatic transfer switch to switchgear control power bus.

3. Control Power Fuses:  Primary and secondary fuses with current-limiting and overload protection.

I. Control Wiring:  Factory installed, complete with bundling, lacing, and protection; and complying with the following:

1. Flexible conductors for No. 8 AWG and smaller, for conductors across hinges and for conductors for interconnections between shipping units.

2. Conductors sized according to NFPA 70 for the duty required.

2.5 CIRCUIT BREAKERS

A. Description:  Comply with IEEE C37.13.

Coordinate first paragraph below with Drawings.

B. Ratings:  As indicated for continuous, interrupting, and short-time current ratings for each circuit breaker; voltage and frequency ratings same as switchgear.

C. Operating Mechanism:  Mechanically and electrically trip-free, stored-energy operating mechanism with the following features:

1. Normal Closing Speed:  Independent of both control and operator.

2. Slow Closing Speed:  Optional with operator for inspection and adjustment.

Select one of two options in subparagraph below to specify manual or electrical operation for circuit breakers.

3. Stored-Energy Mechanism:  [Manually charged] [Electrically charged, with optional manual charging].

Delete subparagraph below if not required.

4. Operation counter.

D. Trip Devices:  Solid-state, overcurrent trip-device system consisting of one or two current transformers or sensors per phase, a release mechanism, and the following features:

Delete subparagraphs below if not required.

1. Functions:  Long-time-delay, short-time-delay, and instantaneous-trip functions, independent of each other in both action and adjustment.

2. Temperature Compensation:  Ensures accuracy and calibration stability from minus 5 to plus 40 deg C.

3. Field-adjustable, time-current characteristics.

4. Current Adjustability:  Dial settings and rating plugs on trip units or sensors on circuit breakers, or a combination of these methods.

5. Three bands, minimum, for long-time- and short-time-delay functions; marked "minimum," "intermediate," and "maximum."

6. Pickup Points:  Five minimum, for long-time- and short-time-trip functions.  Equip short-time-trip function for switchable I2t operation.

7. Pickup Points:  Five minimum, for instantaneous-trip functions.

Coordinate subparagraph and associated subparagraphs below with Drawings.  Indicate circuits with ground-fault protection.  Show type of protection for each circuit where switchgear has more than one type.

8. Ground-fault protection with at least three short-time-delay settings and three trip-time-delay bands; adjustable current pickup.  Arrange to provide protection for the following:

a. Three-wire circuit or system.

b. Four-wire circuit or system.

c. Four-wire, double-ended substation.

9. Trip Indication:  Labeled, battery-powered lights or mechanical targets on trip device to indicate type of fault.

Delete first paragraph below if not required.  Coordinate with Drawings.

E. Auxiliary Contacts:  For interlocking or remote indication of circuit-breaker position, with spare auxiliary switches and other auxiliary switches required for normal circuit-breaker operation, quantity as indicated.  Each consists of two Type "a" and two Type "b" stages (contacts) wired through secondary disconnect devices to a terminal block in stationary housing.

F. Drawout Features:  Circuit-breaker mounting assembly equipped with a racking mechanism to position circuit breaker and hold it rigidly in connected, test, and disconnected positions.  Include the following features:

1. Interlocks:  Prevent movement of circuit breaker to or from connected position when it is closed, and prevent closure of circuit breaker unless it is in connected, test, or disconnected position.

2. Circuit-Breaker Positioning:  An open circuit breaker may be racked to or from connected, test, and disconnected positions only with the associated compartment door closed, unless live parts are covered by a full dead-front shield.  An open circuit breaker may be manually withdrawn to a position for removal from the structure with the door open.  Status for connection devices for different positions includes the following:

a. Test Position:  Primary disconnect devices disengaged, and secondary disconnect devices and ground contact engaged.

b. Disconnected Position:  Primary and secondary devices and ground contact disengaged.

G. Arc Chutes:  Readily removable from associated circuit breaker when it is in disconnected position, and arranged to permit inspection of contacts without removing circuit breaker from switchgear.

H. Padlocking Provisions:  For installing at least three padlocks on each circuit breaker to secure its enclosure and prevent movement of drawout mechanism.

Delete first paragraph below if not required.

I. Operating Handle:  One for each circuit breaker capable of manual operation.

J. Electric Close Button:  One for each electrically operated circuit breaker.

First paragraph below limits competition because some manufacturers will not provide mechanical interlocks.  Edit to suit Project.  See Editing Instruction No. 8 in the Evaluations.

K. Mechanical Interlocking of Circuit Breakers:  Uses a mechanical tripping lever or equivalent design and electrical interlocks.

L. Key Interlocks:  Arranged so keys are attached at devices indicated.  Mountings and hardware are included where future installation of key-interlock devices is indicated.

M. Undervoltage Trip Devices:  Instantaneous, with adjustable pickup voltage.

Delete paragraph above or below.

N. Undervoltage Trip Devices:  Adjustable time-delay and pickup voltage.

O. Shunt-Trip Devices:  Where indicated.

Delete paragraph and subparagraphs below except for fused circuit breakers.

P. Fused Circuit Breakers:  Circuit breaker and fuse combinations complying with requirements for circuit breakers and trip devices and with the following:

1. Fuses:  NEMA FU 1, Class L current limiting, sized to coordinate with and protect associated circuit breaker.

Delete nonapplicable items in first two subparagraphs below.

2. Circuit Breakers with Frame Size 1600 A and Smaller:  Fuses on line side of associated circuit breaker, on a common drawout mounting, arranged so fuses are accessible only when circuit breaker is in disconnected position.

3. Circuit Breakers with Frame Sizes More Than 1600 A:  Fuses and circuit breakers may be installed in separate compartments on separate drawout mountings.  Fuse drawout element is interlocked with associated power circuit breaker to prevent drawing out fuse element unless circuit breaker is in open position.

4. Open-Fuse Trip Device:  Positive means of tripping and holding circuit breaker in open position when a fuse opens.  Open-fuse status is indicated at front of circuit breaker or fuse drawout element.

Q. Indicating Lights:  To indicate circuit breaker is open or closed, for main and bus tie circuit breakers interlocked either with each other or with external devices.

2.6 ACCESSORIES

Delete first paragraph and associated subparagraphs below if not required.

A. Accessory Set:  Furnish tools and miscellaneous items required for circuit-breaker and switchgear test, inspection, maintenance, and operation.

1. Racking handle to manually move circuit breaker between connected and disconnected positions.

2. Portable test set for testing all functions of circuit-breaker, solid-state trip devices without removal from switchgear.

3. Relay and meter test plugs suitable for testing switchgear meters and switchgear class relays.

Delete one of first two, or both, paragraphs below.  Coordinate apparatus space requirements with Drawings.

B. Circuit-Breaker Removal Apparatus:  Portable, floor-supported, roller-base, elevating carriage arranged for moving circuit breakers in and out of compartments.

If paragraph below is used for outdoor switchgear, it must be (walk-in) aisle type.  Coordinate apparatus space requirements with Drawings.

C. Circuit-Breaker Removal Apparatus:  Overhead-circuit-breaker lifting device, track mounted at top front of switchgear and complete with hoist and lifting yokes matching each size of drawout circuit breaker installed.

Coordinate first paragraph below with Drawings.

D. Spare-Fuse Cabinet:  Identified and compartmented steel box, or cabinet with lockable door.

E. Storage for Manual:  Include a rack or holder, near the operating instructions, for a copy of maintenance manual.

2.7 IDENTIFICATION

Delete this Article if not required.

A. Mimic Bus:  Continuous mimic bus, arranged in single-line diagram format, using symbols and lettered designations consistent with approved mimic-bus diagram.

1. Mimic-bus segments coordinated with devices in switchgear sections to which applied, to produce a concise visual presentation of principal switchgear components and connections.

2. Medium:  Painted graphics, as selected by Architect.

3. Color:  Contrasting with factory-finish background; as selected by Architect from manufacturer's full range.

B. System Power Riser Diagrams:  Depict power sources, feeders, distribution components, and major loads.  Include as-built data for low-voltage power switchgear and connections as follows:

1. Frame size of each circuit breaker.

2. Trip rating for each circuit breaker.

3. Conduit and wire size for each feeder.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine elements and surfaces to receive switchgear for compliance with installation tolerances and other conditions affecting performance.

1. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Anchor switchgear assembly to 4-inch (100-mm), channel-iron floor and attach by bolting.

1. Sills:  Select to suit switchgear; level and grout flush into floor or concrete base.

Delete subparagraph below if not required.  Coordinate with Drawings.

2. Concrete Bases:  4 inches (100 mm) high, reinforced, with chamfered edges.  Extend base no more than 2 inches (50 mm) in all directions beyond the maximum dimensions of switchgear, unless otherwise indicated.  Cast anchor-bolt inserts into bases.  Comply with Division 3 Section "Cast-in-Place Concrete."

B. Temporary Lifting Provisions:  Remove temporary lifting eyes, channels, brackets, and temporary blocking of moving parts from switchgear units and components.

3.3 IDENTIFICATION

Select Division 16 Section "Basic Electrical Materials and Methods" for projects with simple requirements and Division 16 Section "Electrical Identification" for projects with complex requirements.

A. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs as specified in Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]."

B. Bus Diagram and Instructions:  Frame and mount under clear acrylic plastic on the front of switchgear.

C. Operating Instructions:  Printed basic instructions for switchgear, including control and key-interlock sequences and emergency procedures.

3.4 CONNECTIONS

Coordinate two paragraphs below with Drawings.

A. Install equipment grounding conductors for switchgear with ground continuity to main electrical ground bus.

B. Tighten bus joints, electrical connectors, and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.5 FIELD QUALITY CONTROL

A. Prepare for acceptance tests as follows:

1. Test insulation resistance for each switchgear bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

Delete paragraph below if independent testing agency is not required.

B. Testing Agency:  Owner will engage a qualified independent testing agency to perform specified testing.

Delete paragraph above or below.  Retain below to include testing agency services as part of the Work.  Delete above and below if Contractor will perform field quality-control testing.

If appropriate and if Contractor's or manufacturer's service agency is considered qualified to perform electrical testing, edit first paragraph below by deleting "independent."

C. Testing Agency:  Engage a qualified independent testing agency to perform specified testing.

D. Testing:  After installing switchgear and after electrical circuitry has been energized, demonstrate product capability and compliance with requirements.

1. Perform each electrical test and visual and mechanical inspection indicated in NETA ATS.  Certify compliance with test parameters.

a. Switchgear:  Perform tests and inspections stated in NETA ATS, Section 7.1.

b. Circuit Breakers:  Perform tests and inspections stated in NETA ATS, Section 7.6.

c. Protective Relays:  Perform tests and inspections stated in NETA ATS, Section 7.9.

d. Instrument Transformers:  Perform tests and inspections stated in NETA ATS, Section 7.10.

e. Metering and Instrumentation:  Perform tests and inspections stated in NETA ATS, Section 7.11.

f. Ground-Fault Systems:  Perform tests and inspections stated in NETA ATS, Section 7.14.

g. Battery Systems:  Perform tests and inspections stated in NETA ATS, Section 7.18.

h. Surge Arresters:  Perform tests and inspections stated in NETA ATS, Section 7.19.

i. Capacitors:  Perform tests and inspections stated in NETA ATS, Section 7.20.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

Select from options below to suit types of switchgear specified.

E. Infrared Scanning:  After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each switchgear.  Remove front and rear panels so joints and connections are accessible to portable scanner.

1. Follow-up Infrared Scanning:  Perform an additional follow-up infrared scan of each switchgear 11 months after date of Substantial Completion.

2. Instrument:  Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values.  Provide calibration record for device.

3. Record of Infrared Scanning:  Prepare a certified report that identifies switchgear checked and that describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

3.6 ADJUSTING

Paragraph below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

A. Set field-adjustable, protective-relay trip characteristics.

3.7 CLEANING

A. On completion of installation, inspect interior and exterior of switchgear.  Remove paint splatters and other spots.  Vacuum dirt and debris; do not use compressed air to assist in cleaning.  Repair exposed surfaces to match original finish.

3.8 PROTECTION

A. Temporary Heating:  Apply temporary heat to maintain temperature according to manufacturer's written instructions.

3.9 STARTUP SERVICES

Delete first paragraph below if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to perform startup service.

B. Verify that switchgear is installed and connected according to the Contract Documents.

Revise first paragraph below if point-to-point verification of all internal control wiring is not required.

C. Verify that electrical control wiring installation complies with manufacturer's submittal by means of point-to-point continuity testing.  Verify that wiring installation complies with requirements in Division 16 Sections.

D. Complete installation and startup checks according to manufacturer's written instructions.

3.10 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain switchgear.

1. Train Owner's maintenance personnel on procedures and schedules for energizing and de-energizing, troubleshooting, servicing, and maintaining equipment and schedules.

2. Review data in maintenance manuals.  Refer to Division 1 Section "Closeout Procedures."

Delete subparagraph above or below depending on which Section is retained in Division 1.

3. Review data in maintenance manuals.  Refer to Division 1 Section "Operation and Maintenance Data."

4. Schedule training with Owner, through Architect, with at least seven days' advance notice.

END OF SECTION 16430

SWITCHGEAR
16430 - 1

