Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16441 - SWITCHBOARDS

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes service and distribution switchboards rated 600 V and less.

Retain below if switchboard contains fusible devices.

B. See Division 16 Section "Fuses" for fuses for fusible devices in switchboards.

1.2 SUBMITTALS

A. Product Data:  For each type of switchboard, and switchboard component indicated.  Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes.

B. Shop Drawings:  For each switchboard and related equipment, include the following:

1. Dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment.  Show tabulations of installed devices, equipment features, and ratings.  Include the following:

a. Bus configuration, current, and voltage ratings.

b. Short-circuit current rating of switchboards and overcurrent protective devices.

Delete first subparagraph below if not required.

c. Utility company's metering provisions with indication of approval by utility company.

Delete first subparagraph below if series rating of overcurrent protective devices is not used.

d. UL listing for series rating of installed devices.

e. Features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.

2. Wiring Diagrams:  Power, signal, and control wiring.

C. Field quality-control testing reports.

D. Operation and maintenance data.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NEMA PB 2.

C. Comply with NFPA 70.

PART 2 -  PRODUCT

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Eaton Corp.; Cutler-Hammer Products.

2. General Electric Co.; Electrical Distribution & Control Div.

3. Siemens Energy & Automation, Inc.

4. Square D Co.

5. <Insert manufacturer.>

2.2 MANUFACTURED UNITS

Edit first paragraph below to define basic configuration of switchboards required for Project.  Coordinate with Drawings.  If more than one configuration is required, indicate in switchboard schedule on Drawings or edit below to describe each type, and provide designations keyed to Drawings.  Coordinate configuration of switchboard with type of overcurrent protective devices to be housed and with available space.  Consult manufacturers to determine layout requirements.  See Evaluations.

A. Switchboard Configuration: Front, [and] [side] [and rear] accessible, with fixed, individually mounted main device, [panel-mounted] [individually mounted] branches, and adjacent vertical sections [front] [and] [rear] aligned.

B. Buses and Bus Connections: Three phase, four wire, unless otherwise indicated.  Materials and Features as follows:

Select main bus rating from first subparagraph below, insert appropriate bus rating, or indicate on Drawings.

1. Main-Bus Continuous Rating:  [4000] [3000] [2500] [2000] [1600] [1200] <Insert rating>  A.

2. Material for Main Bus:  [Hard-drawn copper of 98 percent conductivity] [or] [ tin-plated, high-strength, electrical-grade aluminum alloy].

3. Connections to Main and Feeder Protective Devices:

Delete one or retain both subparagraphs below, depending on editing of "Material for Main Bus" Paragraph above.

a. If bus is aluminum, use copper or tin-plated aluminum for protective device line and load connections.

b. If bus is copper, use copper for protective device line and load connections.

C. Enclosure Finish:  Factory-applied finish in manufacturer's standard gray color over a rust-inhibiting primer on treated metal surface.

D. Barriers:  Between adjacent switchboard sections.

E. Utility Metering Compartment:  Comply with utility company's requirements.  If separate vertical section is required for utility metering, match and align with basic switchboard.

Pull sections in paragraph below are often required when incoming supply is beneath switchboard.

F. Bus Transition and Incoming Pull Sections:  Match and align with basic switchboard.

G. Pull Box on Top of Switchboard:  Provide adequate ventilation to maintain temperature in pull box within same limits as switchboard.

1. Bottom:  Insulating, fire-resistive material with separate holes for cable drops.

H. Cable Supports: Arranged to facilitate cabling and adequate to support cables indicated, including those for future installation.

Delete first paragraph below if front-access sections are specified.

I. Load Terminals:  Insulated, rigidly braced, silver-plated, copper runback bus extensions equipped with pressure connectors for outgoing circuit conductors.

J. Ground Bus:  1/4-by-2-inch (6-by-50-mm) minimum size, drawn-temper copper of 98 percent conductivity, equipped with pressure connectors for feeder and branch-circuit ground conductors.  For busway feeders, extend insulated equipment grounding cable to busway ground connection and support cable at intervals in vertical run.

K. Contact Surfaces of Buses:  Silver plated.

L. Main Phase Buses, Neutral Buses, and Equipment Ground Buses:  Uniform capacity for entire length of switchboard's main and distribution sections. [ Provide for future extensions from both ends.]

M. Neutral Buses:  [50] [100] percent of the ampacity of the phase buses, unless otherwise indicated, equipped with pressure connectors for outgoing circuit neutral cables. [ Bus extension for busway feeder neutral bus is braced.]

Delete paragraph below if future devices are not indicated.

N. Future Devices:  Equip positions with mounting brackets, supports, bus connections, load terminals, and appurtenances rated at maximum capacity available for future unit.

Bus insulation below may not be required by authorities having jurisdiction.  Delete unless Project conditions require additional bus insulation.  Uninsulated buses are manufacturer's standard.

O. Bus-Bar Insulation: Flame-retardant, 105 deg C minimum tape wrapping, or flame-retardant, sprayed-on insulation of same temperature rating, factory-applied to individual bus bars.

2.3 TVSS DEVICES

Delete this Article if not applicable. Coordinate with Drawings.

A. IEEE C62.41, integrally mounted, solid-state, parallel-connected, sine-wave tracking suppression [and filtering ]modules.

Edit ratings and protection modes in two paragraphs and associated subparagraphs below to suit Project.

B. Protection Modes:

1. Line to neutral.

2. Line to ground.

3. Neutral to ground.

C. Minimum Single-Impulse Current Rating:

1. Line to Neutral:  100,000 A.

2. Line to Ground:  100,000 A

3. Neutral to Ground:  50,000 A.

Retain below if filtering is included for TVSS module specified above.  Edit suit Project.

D. EMI/RFI Noise Attenuation Using 50-ohm Insertion Loss Test:  55 dB at 100 kHz.

Retain and edit first two paragraphs below for panels located at or near Category C locations.  For other locations, delete first paragraph and edit second paragraph for appropriate system voltages.  Edit both for clamping voltages suitable for Project.

E. Category C combination wave clamping voltage shall not exceed [600 V, line to neutral and line to ground on 120/208 V systems] [1000 V, line to neutral and line to ground on 277/480 V systems].

F. UL 1449 clamping levels shall not exceed [400 V, line to neutral and line to ground on 120/208 V systems] [800 V, line to neutral and line to ground on 277/480 V systems].

G. Withstand Capability:  3000 Category C surges with less than 5 percent change in clamping voltage.

Select options below to suit Project.

H. Accessories:  Include the following:

1. Form-C contacts, one normally open and one normally closed, for remote monitoring of system operation.  Contacts to reverse position on failure of any surge diversion module.

2. Audible alarm activated on failure of any surge diversion module.

3. Monitoring lights on front panel indicate "normal protection" and "failure of protection module."

4. Six-digit transient-counter set to totalize transient surges that deviate from the sine-wave envelope by more than 125 V.

2.4 OVERCURRENT PROTECTIVE DEVICES

Coordinate this Article with schedules and Drawings.  Delete device types below not used.

A. Molded-Case Circuit Breakers:  NEMA AB 1, with standard frame sizes, trip ratings, and number of poles, and interrupting capacity to meet available fault currents.

1. Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

2. Adjustable Instantaneous-Trip Circuit Breakers:  Magnetic trip element with front-mounted, field-adjustable trip setting.

3. Electronic Trip Unit Circuit Breakers:  RMS sensing; field-replaceable rating plug; with the following field-adjustable settings:

a. Instantaneous trip.

b. Long- and short-time pickup levels.

c. Long- and short-time time adjustments.

d. Ground-fault pickup level, time delay, and I2t response.

4. Current-Limiting Circuit Breakers:  Frame sizes 400 A and smaller; let-through ratings less than NEMA FU 1, RK-5.

5. Integrally Fused Circuit Breakers:  Thermal-magnetic trip element with integral limiter-style fuse listed for use with circuit breaker; trip activation on fuse opening or on opening of fuse compartment door.

6. GFCI Circuit Breakers:  Single- and two-pole configurations with [5] [30]-mA trip sensitivity.

B. Molded-Case Circuit-Breaker Features and Accessories:  Standard frame sizes, trip ratings, and number of poles.

1. Application Listing:  Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

2. Ground-Fault Protection:  [Integrally mounted] [Remote-mounted] sensor, relay, and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

3. Shunt Trip:  120-V trip coil energized from separate circuit, set to trip at [55] [75] percent of rated voltage.

4. Undervoltage Trip:  Set to operate at 35 to 75 percent of rated voltage [without intentional] [with field-adjustable 0.1- to 0.6-second] time delay.

5. Auxiliary Switch:  [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts;  "a" contacts mimic circuit-breaker contacts, "b"contacts operate in reverse of circuit-breaker contacts.

6. Key Interlock Kit:  Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

7. Zone-Selective Interlocking:  Integral with electronic trip unit; for interlocking ground-fault protection function.

C. Enclosed, Insulated-Case Circuit Breaker:  Fixed mounting, manually closed, fully rated, encased-power circuit breaker with interrupting capacity rating to meet available fault current.

1. Two-step, stored-energy closing.

2. Microprocessor-based trip units with interchangeable rating plug, LED trip indicators, and the following field-adjustable settings:

a. Instantaneous trip.

b. Long- and short-time pickup levels.

c. Long- and short-time time adjustments with I2t response.

d. Ground-fault pickup level, time delay, and I2t response.

3. Remote trip indication and control capability.

4. Key Interlock Kit:  Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

5. Zone-Selective Interlocking:  Integral with electronic trip unit; for interlocking ground-fault protection function.

D. Fused Switch:  NEMA KS 1, Type HD; clips to accommodate specified fuses; lockable handle.

2.5 INSTRUMENTATION

A. Instrument Transformers:  NEMA EI 21.1, IEEE C57.13, and the following:

1. Potential Transformers:  Secondary voltage rating of 120 V and NEMA accuracy class of 0.3 with burdens of W, X, and Y.

Coordinate subparagraph below with Drawings and indicate specific accuracy classes and burdens required for each application.

2. Current Transformers:  Ratios shall be as indicated with accuracy class and burden suitable for connected relays, meters, and instruments.

B. Multifunction Digital-Metering Monitor:  Microprocessor-based unit suitable for three- or four-wire systems and with the following features:

1. Switch-selectable digital display of the following values with maximum accuracy tolerances as indicated:

a. Phase Currents, Each Phase:  Plus or minus 1 percent.

b. Phase-to-Phase Voltages, Three Phase:  Plus or minus 1 percent.

c. Phase-to-Neutral Voltages, Three Phase:  Plus or minus 1 percent.

d. Megawatts:  Plus or minus 2 percent.

e. Megavars:  Plus or minus 2 percent.

f. Power Factor:  Plus or minus 2 percent.

g. Frequency:  Plus or minus 0.5 percent.

h. Megawatt Demand:  Plus or minus 2 percent; demand interval programmable from 5 to 60 minutes.

i. Accumulated Energy, Megawatt Hours:  Plus or minus 2 percent.  Accumulated values unaffected by power outages up to 72 hours.

2. Mounting:  Display and control unit flush or semiflush mounted in instrument compartment door.

Delete two paragraphs below and expand metering capability of multifunction metering devices specified above, or revise demand interval and other meter characteristics below to suit Project.

C. Watt-Hour Meters:  Flush or semiflush type, rated 5 A, 120 V, 3 phase, 3 wire, with 3 elements, 15-minute-indicating-demand register, and provision for testing and adding pulse initiation.

D. Recording Demand Meter:  Usable as totalizing relay or as indicating and recording maximum-demand meter with 15-minute interval.  Meter shall count and control a succession of pulses entering two channels.  House in drawout, back-connected case arranged for semiflush mounting.

2.6 CONTROL POWER

Delete this Article if control power external to protective devices is not required, and if no other switchboard equipment requires control power.

A. Control-Power Transformers:  Dry type, mounted in separate compartments for units larger than 3 kV.

B. Control Circuits:  120 V, supplied through secondary disconnecting devices from control-power transformer.

C. Control-Power Fuses:  Primary and secondary fuses for current-limiting and overload protection of transformer and fuses for protection of control circuits.

D. Control Wiring:  Factory installed, with bundling, lacing, and protection included.  Provide flexible conductors for No. 8 AWG and smaller, for conductors across hinges, and for conductors for interconnections between shipping units.

2.7 ACCESSORY COMPONENTS

A. Accessory Set:  Tools and miscellaneous items required for overcurrent protective device test, inspection, maintenance, and operation.

Delete first paragraph below unless circuit breakers have electronic trip units.

B. Portable Test Set:  To test functions of solid-state trip devices without removal from switchboard.  Include relay and meter test plugs suitable for testing switchboard meters and switchboard class relays.

C. Spare-Fuse Cabinet:  Suitably identified, wall-mounted, lockable, compartmented steel box or cabinet.  Arrange for wall mounting.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install switchboards and accessories according to NEMA PB 2.1.

B. Support switchboards on concrete bases, 4-inch (100-mm) nominal thickness.

C. Temporary Lifting Provisions:  Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from switchboard units and components.

D. Operating Instructions:  Frame and mount the printed basic operating instructions for switchboards, including control and key interlocking sequences and emergency procedures.  Fabricate frame of finished wood or metal and cover instructions with clear acrylic plastic.  Mount on front of switchboards.

3.2 IDENTIFICATION

In first paragraph below, select Division 16 Section "Basic Electrical Materials and Methods" for projects with simple requirements and Division 16 Section "Electrical Identification" for projects with complex requirements.

A. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs as specified in Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]."

B. Switchboard Nameplates:  Label each switchboard compartment with engraved metal or laminated-plastic nameplate mounted with corrosion-resistant screws.

3.3 FIELD QUALITY CONTROL

A. Prepare for acceptance tests as follows:

1. Test insulation resistance for each switchboard bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

B. Testing:  After installing switchboards and after electrical circuitry has been energized, demonstrate product capability and compliance with requirements.

1. Procedures:  Perform each electrical test and visual and mechanical inspection indicated in NETA ATS, Sections 7.1, 7.5, 7.6, 7.9, 7.10, 7.11, and 7.14 as appropriate.  Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance;  otherwise, replace with new units and retest.

Select from options in first paragraph below to suit types of switchboards specified.

C. Infrared Scanning:  After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each switchboard.  Remove [front] [front and rear] panels so joints and connections are accessible to portable scanner.

1. Instrument:  Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values.  Provide calibration record for device.

2. Record of Infrared Scanning:  Prepare a certified report that identifies switchboards checked and that describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

D. Report test results in writing.

3.4 ADJUSTING

Below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

A. Set field-adjustable switches and circuit-breaker trip ranges.

END OF SECTION 16441

SWITCHBOARDS
16441 - 1

