Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16443 - MOTOR-CONTROL CENTERS

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes motor-control centers for use on ac circuits rated 600 V and less.

B. See Division 16 Section "Electrical Power Monitoring and Control" for monitoring and control of motor circuits.

C. See Division 16 Section "Transient Voltage Suppression" for low-voltage power, control, and communication surge suppressors.

1.2 SUBMITTALS

A. Product Data:  For each type of controller and each type of motor-control center indicated.

B. Shop Drawings:  For each motor-control center.

1. Dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment.  Show tabulations of installed devices, equipment features, and ratings.  Include the following:

a. Each installed unit's type and details.

b. Nameplate legends.

c. Short-circuit current ratings of buses and installed units.

d. Vertical and horizontal bus capacities.

Delete first subparagraph below if series rating of overcurrent protective devices is not used or if combination controllers are not used.

e. UL listing for series rating of overcurrent protective devices in combination controllers.

f. Features, characteristics, ratings, and factory settings of each motor-control center unit.

2. Wiring Diagrams:  Power, signal, and control wiring.

C. Field quality-control test reports.

D. Operation and maintenance data.

Coordinate below with Part 3.

E. Load-Current and Overload-Relay Heater List:  Compile after motors have been installed and arrange to demonstrate that selection of heaters suits actual motor nameplate full-load currents.

1.3 QUALITY ASSURANCE

A. Source Limitations:  Obtain controllers of a single type through one source from a single manufacturer.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Comply with NFPA 70.

Motor-control centers with the same functional characteristics may vary slightly in length and depth among manufacturers.  If installation space is severely limited, show maximum dimensions on Drawings, ensure that equipment is available to fit, and retain below.  Delete below if space is not a concern.

D. Product Selection for Restricted Space:  Drawings indicate maximum dimensions for motor-control centers, including clearances between motor-control centers, and for adjacent surfaces and other items. Comply with indicated maximum dimensions.

1.4 COORDINATION

Revise two paragraphs below to refer to other Divisions, such as Division 14 for conveyor systems, if control coordination is required.

A. Coordinate features of motor-control centers, installed units, and accessory devices with pilot devices and control circuits to which they connect.

B. Coordinate features, accessories, and functions of each motor-control center, each controller, and each installed unit with ratings and characteristics of supply circuit, motor, required control sequence, and duty cycle of motor and load.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Only manufacturers of motor-control centers complying with NEMA standards are included below.  Manufacturers of motor-control centers using only International Electrotechnical Commission components are not included.  See the Evaluations in Division 16 Section "Enclosed Controllers."

1. ABB Power Distribution, Inc.; ABB Control, Inc. Subsidiary.

2. Eaton Corp.; Cutler-Hammer Products.

3. General Electrical Distribution & Control.

4. Rockwell Automation Allen-Bradley Co.; Industrial Control Group.

5. Siemens/Furnas Controls.

6. Square D Co.

7. <Insert manufacturer.>

2.2 MOTOR-CONTROL CENTERS

See Evaluations for a discussion of alternatives.

A. Wiring:  NEMA ICS 3, Class  [I, Type A] [I, Type B] [I, Type C] [II, Type B] [II, Type C].

Revise paragraph and subparagraphs below if other-than-routine indoor installation conditions apply.  Coordinate with Drawings.  See Evaluations for other enclosure types.

B. Enclosures:  Flush- or surface-mounted cabinets as indicated.  NEMA 250, Type 1, unless otherwise indicated to comply with environmental conditions at installed location.

Delete items below if not applicable.  Add other Project-specific requirements.

1. Outdoor Locations:  NEMA 250, Type 3R.

2. Compartments:  Modular; individual doors with concealed hinges and quick-captive screw fasteners.  Interlocks on combination controller units requiring disconnecting means in off position before door can be opened or closed, except by operating a permissive release device.

3. Interchangeability:  Compartments constructed to allow for removal of units without opening adjacent doors, disconnecting adjacent compartments, or disturbing operation of other units in motor-control center.  Interchangeability of units requiring the same size compartment and constructed to permit ready rearrangement of units, such as replacing three single units with a unit requiring three spaces, without cutting or welding.

4. Wiring Spaces:  Wiring channel in each vertical section for vertical and horizontal wiring to each unit compartment; supports to hold wiring in place.

Coordinate below with Drawings or state fault current below.

C. Short-Circuit Current Rating for Each Section:  Equal to or greater than indicated available fault current in symmetrical amperes at motor-control center location.

2.3 BUSES

A. Material:  Plated [copper] [aluminum].

B. Ampacity Ratings:  As indicated for horizontal and vertical main buses.

C. Neutral Buses:  [Full] [Half] size.

D. Equipment Ground Bus:  Noninsulated, horizontal copper bus 2 by 1/4 inch (50 by 6 mm), minimum.

E. Horizontal Bus Arrangement:  Main phase, neutral and ground buses extended with same capacity the entire length of motor-control center, with provision for future extension at both ends by bolt holes and captive bus splice sections or equivalent.

Coordinate below with Drawings.

F. Short-Circuit Withstand Rating:  Same as short-circuit current rating of section.

2.4 FUNCTIONAL FEATURES

Delete paragraph below if not applicable.  Coordinate with Drawings.

A. Description:  Modular arrangement of controllers, control devices, overcurrent protective devices, transformers, panelboards, instruments, indicating panels, blank panels, and other items mounted in compartments of motor-control center.

Coordinate two paragraphs and associated subparagraphs below with Drawings.

B. Controller Units:  Combination controller units of types and with features, ratings, and circuit assignments indicated.

1. Install units with full-voltage, across-the-line, magnetic controllers up to and including Size 3 on drawout mountings with connectors that automatically line up and connect with vertical-section buses while being racked into their normal, energized positions.

2. Provide units with short-circuit current ratings equal to or greater than short-circuit current rating of motor-control center section.

3. Equip units in Type B and Type C motor-control centers with pull-apart terminal strips or drawout terminal boards for external control connections.

C. Overcurrent Protective Devices:  Individual feeder-tap units through 225-A rating shall have drawout mountings with connectors that automatically line up and connect with vertical-section buses while being racked into their normal, energized positions.

Coordinate two paragraphs below with Drawings.  Indicate, in schedule, sizes of future controllers to be accommodated.

D. Spaces and Blank Units:  Compartments fully bused and equipped with guide rails or equivalent, ready for insertion of drawout units.

E. Spare Units:  Type, sizes, and ratings indicated; installed in compartments indicated "spare."

2.5 MAGNETIC MOTOR CONTROLLERS

Coordinate two paragraphs below with Drawings.

A. Description:  NEMA ICS 2, Class A, full voltage, nonreversing, across the line, unless otherwise indicated.

B. Control Circuit:  120 V; obtained from [integral control power transformer] <Insert source of control power> with a control power [transformer] [source] of sufficient capacity to operate connected pilot, indicating and control devices, plus 100 percent spare capacity.

Indicate requirements for overcurrent protective devices on Drawings.

C. Combination Controller:  Factory-assembled combination controller and disconnect switch.

1. Fusible Disconnecting Means:  NEMA KS 1, heavy-duty, fusible switch with rejection-type fuse clips rated for fuses.  Select and size fuses to provide Type 2 protection according to IEC 947-4-1, as certified by a nationally recognized testing laboratory.

2. Nonfusible Disconnecting Means:  NEMA KS 1, heavy-duty, nonfusible switch.

3. Circuit-Breaker Disconnecting Means:  NEMA AB 1, motor-circuit protector with field-adjustable, short-circuit trip coordinated with motor locked-rotor amperes.

Select trip class from options listed in first two paragraphs below.  See Evaluations for discussion.

D. Overload Relay:  Ambient-compensated type with inverse-time-current characteristic and NEMA ICS 2, Class  [10] [20] [30] tripping characteristic.  Provide with heaters or sensors in each phase matched to nameplate full-load current of specific motor to which they connect and with appropriate adjustment for duty cycle.

Select paragraph above or below.

E. Adjustable Overload Relay:  Dip switch selectable for motor running overload protection with NEMA ICS 2, Class  [10] [20] [30] tripping characteristic, and selected to protect motor against voltage and current unbalance and single phasing.  Provide relay with Class II ground-fault protection, with start and run delays to prevent nuisance trip on starting.

Revise controller specifications to suit Project.  Delete types below if not used.  Coordinate with Drawings.  See Evaluations for selection considerations.

F. Star-Delta Controller:  NEMA ICS 2, closed transition with adjustable time delay.

G. Part-Winding Controller:  NEMA ICS 2, closed transition with separate overload relays for starting and running sequences.

H. Autotransformer Reduced-Voltage Controller:  NEMA ICS 2, closed transition.

2.6 FEEDER OVERCURRENT PROTECTION

Edit this Article to suit Project.  Coordinate with Drawings.

A. Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

1. Adjustable Instantaneous-Trip Circuit Breakers:  Magnetic trip element with front-mounted, field-adjustable trip setting.

2. Electronic Trip Unit Circuit Breakers:  RMS sensing; field-replaceable rating plug; with the following field-adjustable settings:

a. Instantaneous trip.

b. Long- and short-time pickup levels.

c. Long- and short-time time adjustments.

d. Ground-fault pickup level, time delay, and I2t response.

3. Current-Limiting Circuit Breakers:  Frame sizes 400 A and smaller; let-through ratings less than NEMA FU 1, RK-5.

4. Integrally Fused Circuit Breakers:  Thermal-magnetic trip element with integral limiter-style fuse listed for use with circuit breaker; trip activation on fuse opening or on opening of fuse compartment door.

5. GFCI Circuit Breakers:  Single- and two-pole configurations with [5] [30]-mA trip sensitivity.

6. Molded-Case Switch:  Molded-case circuit breaker without trip units.

B. Molded-Case, Circuit-Breaker Features and Accessories:  Standard frame sizes, trip ratings, and number of poles.

1. Lugs:  [Mechanical] [Compression] style, suitable for number, size, trip ratings, and material of conductors.

2. Application Listing:  Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

3. Ground-Fault Protection:  [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

4. Communication Capability:  [Circuit-breaker-mounted] [Universal-mounted] [Integral] [Din-rail-mounted] communication module with functions and features compatible with power monitoring and control system.

5. Shunt Trip:  120-V trip coil energized from separate circuit, set to trip at [55] [75] percent of rated voltage.

6. Undervoltage Trip:  Set to operate at 35 to 75 percent of rated voltage [without intentional] [with field-adjustable 0.1- to 0.6-second] time delay.

7. Auxiliary Switch:  [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts;  "a" contacts mimic circuit-breaker contacts; "b"contacts operate in reverse of circuit-breaker contacts.

8. Key Interlock Kit:  Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

9. Zone-Selective Interlocking:  Integral with electronic trip unit; for interlocking ground-fault protection function.

C. Fusible Switch:  NEMA KS 1, Type HD, clips to accommodate specified fuses with lockable handle.

2.7 MOTOR-CONTROL CENTER ACCESSORIES

A. Devices shall be factory installed in controller enclosure, unless otherwise indicated.

Delete six paragraphs below if not applicable.  Coordinate with Drawings.

B. Push-Button Stations, Pilot Lights, and Selector Switches:  NEMA ICS 2, heavy-duty type.

C. Stop and Lockout Push-Button Station:  Momentary-break, push-button station with a factory-applied hasp arranged so padlock can be used to lock push button in depressed position with control circuit open.

D. Control Relays:  Auxiliary and adjustable time-delay relays.

E. Phase-Failure and Undervoltage Relays:  Solid-state sensing circuit with isolated output contacts for hard-wired connection.  Provide adjustable undervoltage setting.

Retain paragraph below with three external current transformers.

F. Current-Sensing, Phase-Failure Relays:  Solid-state sensing circuit with isolated output contacts for hard-wired connection; arranged to operate on phase failure, phase reversal, current unbalance of from 30 to 40 percent, or loss of supply voltage; with adjustable response delay.

Select cabinet type from options below.  Coordinate with Drawings.  Delete if no fuses are used for power or control circuits.

G. Spare-Fuse Cabinet:  Identified [and compartmented steel box] [cabinet with hinged lockable door].

PART 3 -  EXECUTION

3.1 APPLICATIONS

Delete this Article or revise to suit office practice, Project, and Drawing Coordination.  Delete if controllers and control devices and their types and features are delineated on Drawings.

A. Select features of each controller to coordinate with ratings and characteristics of supply circuit and motor; required control sequence; duty cycle of motor, drive, and load; and configuration of pilot device and control circuit affecting controller functions.

B. Select horsepower rating of controllers to suit motor controlled.

3.2 INSTALLATION

Coordinate this Article with Drawings.

A. See Division 16 Section "Basic Electrical Materials and Methods" for general installation instructions.

Delete paragraph below if not required and specify alternative anchoring.  Coordinate mounting methods with Drawings.  Add requirements for special anchorage and seismic restraint, if applicable.

B. Anchor each motor-control center assembly to steel-channel sills arranged and sized according to manufacturer's written instructions.  Attach by bolting.  Level and grout sills flush with motor-control center mounting surface.

Coordinate mounting and anchoring of motor-control centers with drawing details.  If drawing details are explicit, delete paragraph below.

C. Install motor-control centers on concrete bases complying with Division 3 Section "Cast-in-Place Concrete."

Retain first paragraph below if seismic controls are Project requirement.  Coordinate with Drawings.

D. Comply with mounting and anchoring requirements specified in Division 16 Section "Seismic Controls for Electrical Work."

E. Controller Fuses:  Install fuses in each fusible switch.  Comply with requirements in Division 16 Section "Fuses."

3.3 IDENTIFICATION

A. Identify motor-control center, motor-control center components, and control wiring according to Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]."

Show specific information to be included in framed instructions on Drawings.  If not required, delete below.

B. Operating Instructions:  Frame printed operating instructions for motor-control centers, including control sequences and emergency procedures.  Fabricate frame of finished metal and cover instructions with clear acrylic plastic.  Mount on front of motor-control centers.

3.4 CONTROL WIRING INSTALLATION

Delete this Article if not applicable or if remote control or indication is not required.

A. Install wiring between motor-control devices according to Division 16 Section "Conductors and Cables."

B. Bundle, train, and support wiring in enclosures.

C. Connect hand-off-automatic switch and other automatic-control devices where available.

1. Connect selector switches to bypass only manual- and automatic-control devices that have no safety functions when switch is in hand position.

2. Connect selector switches with motor-control circuit in both hand and automatic positions for safety-type control devices such as low- and high-pressure cutouts, high-temperature cutouts, and motor overload protectors.

3.5 FIELD QUALITY CONTROL

A. Testing:  Perform the following field quality-control testing:

Retain subparagraphs below with paragraph above.  Edit to suit Project.

1. Perform each electrical test and visual and mechanical inspection indicated in NETA ATS, Sections 7.5, 7.6, and 7.16.

2. Certify compliance with test parameters.

3. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance;  otherwise, replace with new units and retest.

B. Report test results in writing.

END OF SECTION 16443

MOTOR-CONTROL CENTERS
16443 - 1

