Copyright 1996 AIA
MASTERSPEC
6/96


Copyright 1996, The American Institute of Architects (AIA)

SECTION 16461 - DRY-TYPE TRANSFORMERS (1000 V AND LESS)

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

Edit below to suit Project.

A. This Section includes dry-type distribution and specialty transformers rated 1000 V and less.

1.3 SUBMITTALS

A. Product Data:  Include data on features, components, ratings, and performance for each type of transformer specified.  Include dimensioned plans, sections, and elevation views.  Show minimum clearances and installed devices and features.

B. Wiring Diagrams:  Detail wiring and identify terminals for tap changing and connecting field-installed wiring.

C. Product Certificates:  Signed by manufacturers of transformers certifying that the products furnished comply with requirements.

D. Qualification Data:  For firms and persons specified in "Quality Assurance" Article.

Delete below if factory test reports are not required.  Delete "design and" if reports of routine tests suffice.

E. Factory Test Reports:  Certified copies of manufacturer's design and routine factory tests required by referenced standards.

Delete below unless equipment sound-level ratings lower than NEMA ST 20 are specified.  Coordinate with Part 2 and with Drawings.  See Editing Instruction No. 2 in the Evaluations.

F. Sound-Level Test Reports:  Certified copies of manufacturer's sound-level tests applicable to equipment for this Project.

G. Field Test Reports:  Indicate and interpret test results for tests specified in Part 3.

H. Maintenance Data:  For transformers to include in the maintenance manuals specified in Division 1.

1.4 QUALITY ASSURANCE

Delete paragraph below if an independent testing agency is not required or if Owner will engage an independent testing agency.

A. Testing Agency Qualifications:  In addition to requirements specified in Division 1 Section "Quality Control," an independent testing agency shall meet OSHA criteria for accreditation of testing laboratories, Title 29, Part 1907; or shall be a full-member company of the InterNational Electrical Testing Association.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies, to supervise on-site testing specified in Part 3.

B. Listing and Labeling:  Provide transformers specified in this Section that are listed and labeled.

1. The Terms "Listed" and "Labeled":  As defined in NFPA 70, Article 100.

Subparagraph below is required by some Federal agencies.

2. Listing and Labeling Agency Qualifications:  A "Nationally Recognized Testing Laboratory" as defined in OSHA Regulation 1910.7.

C. Comply with IEEE C2.

D. Comply with NFPA 70.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Temporary Heating:  Apply temporary heat according to manufacturer's written instructions within the enclosure of each ventilated-type unit throughout periods during which equipment is not energized and is not in a space that is continuously under normal control of temperature and humidity.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering transformers that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

B. Manufacturers:  Subject to compliance with requirements, provide transformers by one the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1. Acme Electric Corp.; Transformer Division.

2. Bryant Electric.

3. Challenger Electrical Equipment Corp.

4. Computer Power Inc.

5. Controlled Power Co.

6. Cutler-Hammer/Eaton Corp.

7. Federal Pacific Co.; Line Power Mfg. Corp. Subsidiary.

8. GE Electrical Distribution & Control.

9. Hammond Co.; Matra Electric, Inc.

10. MagneTek Inc.

11. Micron Industries Corp.

12. Siemens Energy & Automation, Inc.

13. Sola/Hevi-Duty Electric.

14. Square D; Groupe Schneider.

15. Uptegraff:  R.E. Uptegraff Mfg. Co.

16. Virginia Transformer Corp.

2.2 TRANSFORMERS, GENERAL

A. Description:  Factory-assembled and -tested, air-cooled units of types specified, designed for 60-Hz service.

B. Cores:  Grain-oriented, nonaging silicon steel.

Transformers with copper coils cost about 40 percent more and have about 20 percent greater weight than those with aluminum coils.  Enclosures are usually the same size for the same ratings for both coil materials.  Aluminum is the standard coil material for most manufacturers, but most will provide copper coils if specified.  Both types are fitted to connect to circuit conductors of either material.

C. Coils:  [Electrical grade aluminum] [Copper].  Continuous windings without splices, except for taps.

D. Internal Coil Connections:  Brazed or pressure type.

E. Enclosure:  Class complies with NEMA 250 for the environment in which installed.

Delete below unless one or more transformers are indicated to be low-sound-level units.  See Editing Instruction No. 2 in the Evaluations.  Coordinate with Drawings.

F. Low-Sound-Level Units:  Minimum of 3 dBA less than NEMA ST 20 standard sound levels when factory tested according to IEEE C57.12.91.

2.3 GENERAL-PURPOSE DISTRIBUTION AND POWER TRANSFORMERS

A. Comply with NEMA ST 20 and list and label as complying with UL 1561.

B. Cores:  One leg per phase.

C. Windings:  One coil per phase in primary and secondary.

If all transformers have same enclosure, select from 5 paragraphs below.  If enclosures vary, delete all and show on Drawings.

D. Enclosure:  Indoor, ventilated.

E. Enclosure:  Indoor, ventilated, dripproof.

F. Enclosure:  Outdoor, ventilated, raintight, NEMA 250, Type 3R.

G. Enclosure:  Totally enclosed, nonventilated.

H. Enclosure:  Totally enclosed, nonventilated, suitable for outdoor use.

I. Insulation Class:  185 or 220 deg C class for transformers 15 kVA or smaller; 220 deg C class for transformers larger than 15 kVA.

If all transformers have same insulation temperature rise, select from 3 subparagraphs below.  If temperature rises vary, delete all and show on Drawings.  See Editing Instruction No. 3 in the Evaluations.

1. Rated Temperature Rise:  80 deg C maximum rise above 40 deg C.

2. Rated Temperature Rise:  115 deg C maximum rise above 40 deg C.

3. Rated Temperature Rise:  150 deg C maximum rise above 40 deg C, for 220 deg C class insulation; 115 deg C maximum rise for 185 deg C class insulation.

J. Taps:  For transformers 3 kVA and larger, full-capacity taps in high-voltage windings are as follows:

If all transformers have same voltage taps, select from 4 subparagraphs below.  If taps vary, delete all and show on Drawings.  First item is standard.

1. Taps, 3 through 25 kVA:  Two 5-percent taps below rated high voltage.

2. Taps, 3 through 10 kVA:  Two 5-percent taps below rated high voltage.

3. Taps, 15 through 500 kVA:  Six 2.5-percent taps, 2 above and 4 below rated high voltage.

4. Taps, 750 kVA and Above:  Four 2.5-percent taps, 2 above and 2 below rated high voltage.

Select features from 4 paragraphs below.  Coordinate with Drawings.

Retain below where some transformers will supply significant nonsinusoidal load current.  Show transformer K-factor ratings on Drawings or in a schedule.  See Evaluations.

K. K-Factor Rating:  Transformers indicated to be K-factor rated are listed to comply with UL 1561 requirements for nonsinusoidal load current handling capability to the degree defined by the designated K-factor.

1. Transformer design prevents overheating when carrying full load with harmonic content corresponding to the designated K-factor.

2. Nameplate states the designated K-factor of the transformer.

Include shielding if necessary to reduce conducted, common-mode, high-frequency transient noise to sensitive downstream loads.  See Evaluations.

L. Electrostatic Shielding:  Each winding is independently single shielded with a full-width copper electrostatic shield arranged to minimize interwinding capacitance.

1. Coil leads and terminal strips are arranged to minimize capacitive coupling between input and output connections.

2. Shield Terminal:  Separate; marked "Shield" for grounding connection.

3. Capacitance:  Shield limits capacitance between primary and secondary to a maximum of 33 picofarads over a frequency range of 20 Hz to 1 MHz.

4. Common-Mode Noise Attenuation:  Minus 120 dB minimum, 0.5 to 1.5 kHz; minus 65 dB minimum, 1.5 to 100 kHz.

5. Normal-Mode Noise Attenuation:  Minus 52 dB minimum, 1.5 to 10 kHz.

Coordinate paragraph below with Drawings.

M. Wall-Mounting Brackets:  Manufacturer's standard brackets for transformers up to 75 kVA.

Omit below except for installations in tropical environments.

N. Fungus Proofing:  Permanent fungicidal treatment for coil and core.

2.4 BUCK-BOOST TRANSFORMERS

A. Units comply with NEMA ST 1 and are listed and labeled as complying with UL 506 or UL 1561.

Coordinate below with Drawings.

B. Description:  Self-cooled dry type, rated for continuous duty, and connected as autotransformers to provide the percentage of buck or boost indicated.

2.5 CONTROL AND SIGNAL TRANSFORMERS

A. Units comply with NEMA ST 1 and are listed and labeled as complying with UL 506.

Coordinate paragraphs below with Drawings.

B. Ratings:  Continuous duty.  If rating is not indicated, provide capacity exceeding peak load by 50 percent minimum.

C. Description:  Self-cooled, 2 windings.

2.6 FINISHES

A. Indoor Units:  Manufacturer's standard paint over corrosion-resistant pretreatment and primer.

B. Outdoor Units:  Comply with ANSI C57.12.28.

2.7 SOURCE QUALITY CONTROL

A. Factory Tests:  Design and routine tests comply with referenced standards.

Delete below unless sound level is critical and Project budget covers cost of tests.  See Editing Instruction No. 2 in the Evaluations.

B. Factory Sound-Level Tests:  Conduct sound-level tests on equipment for this Project if specified sound levels are below standard ratings.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Comply with safety requirements of IEEE C2.

B. Arrange equipment to provide adequate spacing for access and for circulation of cooling air.

Revise paragraph below if identification requirements are specified in Division 16 Section "Basic Electrical Materials and Methods."

C. Identify transformers and install warning signs according to Division 16 Section "Electrical Identification."

D. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.2 GROUNDING

A. Separately Derived Systems:  Comply with NFPA 70 requirements for connecting to grounding electrodes and for bonding to metallic piping near the transformer.

Select paragraph above or below and coordinate with Drawings to minimize confusion during construction due to recent code changes.

B. Separately Derived Systems:  Make grounding connections to grounding electrodes and bonding connections to metallic piping as indicated and to comply with NFPA 70.

C. Comply with Division 16 Section "Grounding" for materials and installation requirements.

3.3 FIELD QUALITY CONTROL

Delete paragraph below if not required.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to supervise the field assembly and connection of components, and the testing and adjusting of transformer components and accessories.

B. Testing Agency:  Owner will engage a qualified independent testing agency to perform field quality-control testing.

Delete paragraph above or below.  Retain below if testing agency services are in this Contract.  Delete both if Contractor will perform field quality-control testing.

C. Testing Agency:  Engage a qualified independent testing agency to perform field quality-control testing.

D. Test Objectives:  To ensure transformer is operational within industry and manufacturer's tolerances, is installed according to the Contract Documents, and is suitable for energizing.

E. Test Labeling:  On satisfactory completion of tests for each transformer, attach a dated and signed "Satisfactory Test" label to tested component.

F. Schedule tests and provide notification at least 7 days in advance of test commencement.

G. Report:  Submit a written report of observations and tests.  Report defective materials and installation.

H. Tests:  Include the following minimum inspections and tests according to manufacturer's written instructions.  Comply with IEEE C57.12.91 for test methods and data correction factors.

1. Inspect accessible components for cleanliness, mechanical and electrical integrity, and damage or deterioration.  Verify that temporary shipping bracing has been removed.  Include internal inspection through access panels and covers.

2. Inspect bolted electrical connections for tightness according to manufacturer's published torque values or, if not available, those specified in UL 486A and UL 486B.

3. Insulation Resistance:  Perform megohmmeter tests of primary and secondary winding to winding and winding to ground.

a. Minimum Test Voltage:  1000 V, dc.

b. Minimum Insulation Resistance:  500 megohms.

c. Duration of Each Test:  10 minutes.

d. Temperature Correction:  Correct results for test temperature deviation from 20 deg C standard.

I. Test Failures:  Compare test results with specified performance or manufacturer's data.  Correct deficiencies identified by tests and retest.  Verify that transformers meet specified requirements.

3.4 CLEANING

A. On completion of installation, inspect components.  Remove paint splatters and other spots, dirt, and debris.  Repair scratches and mars on finish to match original finish.  Clean components internally using methods and materials recommended by manufacturer.

3.5 ADJUSTING

A. After installing and cleaning, touch up scratches and mars on finish to match original finish.

B. Adjust transformer taps to provide optimum voltage conditions at utilization equipment throughout normal operating cycle of facility.  Record primary and secondary voltages and tap settings and submit with test results.

Delete paragraph below unless buck-boost transformers are specified.

C. Adjust buck-boost transformer connections to provide optimum voltage conditions at utilization equipment throughout normal operating cycle of facility.

D. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in readjusting transformer tap settings to suit actual occupied conditions.  Provide up to 2 visits to Project site for this purpose without additional cost.

1. Voltage Recordings:  Contractor performed.  Provide up to 48 hours of recording on the low-voltage system of each medium-voltage transformer.

2. Point of Measurement:  Make voltage recordings at load outlets selected by Owner.

END OF SECTION 16461

DRY-TYPE TRANSFORMERS (1000 V AND LESS)
16461 - 1

