Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16461 - DRY-TYPE TRANSFORMERS (1000 V AND LESS)

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes dry-type distribution and specialty transformers rated 1000 V and less.

1.2 SUBMITTALS

A. Product Data:  For each type of dry-type transformer product indicated.

B. Shop Drawings:  Include plans, elevations, sections, and details of installation.

1. Wiring Diagrams:  Power, signal, and control wiring.

C. Field quality-control test reports.

D. Operation and maintenance data.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Acme Electric Corp.; Transformer Division.

2. Bryant Electric.

3. Challenger Electrical Equipment Corp.

4. Computer Power Inc.

5. Controlled Power Co.

6. Cutler-Hammer/Eaton Corp.

7. Federal Pacific Co.; Line Power Mfg. Corp. Subsidiary.

8. GE Electrical Distribution & Control.

9. Hammond Co.; Matra Electric, Inc.

10. MagneTek Inc.

11. Micron Industries Corp.

12. Siemens Energy & Automation, Inc.

13. Sola/Hevi-Duty Electric.

14. Square D; Groupe Schneider.

15. Uptegraff, R. E. Mfg. Co.

16. Virginia Transformer Corp.

17. <Insert manufacturer.>

2.2 TRANSFORMERS, GENERAL

A. Description:  Factory-assembled and -tested, air-cooled units of types specified, designed for 60-Hz service.

B. Cores:  Grain-oriented, nonaging silicon steel.

Edit first paragraph below if copper coils are desired.  Transformers with copper coils cost about 40 percent more and have about 20 percent greater weight than those with aluminum coils.  Enclosures are usually the same size for the same ratings for both coil materials.  Aluminum is the standard coil material for most manufacturers, but most will provide copper coils if specified.  Both types are fitted to connect to circuit conductors of either material.

C. Coils:  Electrical grade aluminum.  Continuous windings without splices, except for taps.

D. Internal Coil Connections:  Brazed or pressure type.

2.3 GENERAL-PURPOSE DISTRIBUTION AND POWER TRANSFORMERS

A. Comply with NEMA ST 20 and list and label as complying with UL 1561.

B. Cores:  One leg per phase.

C. Windings:  One coil per phase in primary and secondary.

If all transformers have same enclosure, edit first paragraph below.  If enclosures vary, delete paragraph and show on Drawings.

D. Enclosure:  [Indoor, ventilated] [Indoor, ventilated, dripproof] [Outdoor, ventilated, raintight, NEMA 250, Type 3R] [totally enclosed, nonventilated] [Totally enclosed, nonventilated, suitable for outdoor use].

E. Insulation Class:  185 or 220 deg C class for transformers 15 kVA or smaller; 220 deg C class for transformers larger than 15 kVA.

If all transformers have same insulation temperature rise, select from two subparagraphs below.  If temperature rises vary, delete all and show on Drawings.  See Editing Instruction No. 3 in the Evaluations.

1. Rated Temperature Rise:  [80] [115] deg C maximum rise above 40 deg C.

2. Rated Temperature Rise:  150 deg C maximum rise above 40 deg C, for 220 deg C class insulation; 115 deg C maximum rise for 185 deg C class insulation.

F. Taps:  For transformers 3 kVA and larger, full-capacity taps in high-voltage windings are as follows:

If all transformers have same voltage taps, select from three subparagraphs below.  If taps vary, delete all and show on Drawings.  First item is standard.

1. Taps, 3 through [10] [25]  kVA:  Two 5-percent taps below rated high voltage.

2. Taps, 15 through 500 kVA:  Six 2.5-percent taps, 2 above and 4 below rated high voltage.

3. Taps, 750 kVA and Above:  Four 2.5-percent taps, 2 above and 2 below rated high voltage.

Retain paragraph and subparagraphs below where some transformers will supply significant nonsinusoidal load current.  Show transformer K-factor ratings on Drawings or in a schedule.  See Evaluations.

G. K-Factor Rating:  Transformers indicated to be K-factor rated are listed to comply with UL 1561 requirements for nonsinusoidal load current handling capability to the deg ree defined by the designated K-factor.

1. Transformer design prevents overheating when carrying full load with harmonic content corresponding to the designated K-factor.

2. Nameplate states the designated K-factor of the transformer.

Coordinate below with Drawings.

H. Wall-Mounting Brackets:  Manufacturer's standard brackets for transformers up to 75 kVA.

2.4 FINISHES

A. Indoor Units:  Manufacturer's standard paint over corrosion-resistant pretreatment and primer.

B. Outdoor Units:  Comply with ANSI C57.12.28.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Arrange equipment to provide adequate spacing for access and for circulation of cooling air.

B. Identify transformers and install warning signs according to Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]."

3.2 FIELD QUALITY CONTROL

A. Test Objectives:  To ensure transformer is operational within industry and manufacturer's tolerances, is installed according to the Contract Documents, and is suitable for energizing.

B. Schedule tests and provide notification at least seven days in advance of test commencement.

C. Report:  Submit a written report of observations and tests.  Report defective materials and installation.

D. Tests:  Include the following minimum tests and inspections according to manufacturer's written instructions.  Comply with IEEE C57.12.91 for test methods and data correction factors.

1. Inspect accessible components for cleanliness, mechanical and electrical integrity, and damage or deterioration.  Verify that temporary shipping bracing has been removed.  Include internal inspection through access panels and covers.

2. Inspect bolted electrical connections for tightness according to manufacturer's published torque values or, if not available, those specified in UL 486A and UL 486B.

3. Insulation Resistance:  Perform megohmmeter tests of primary and secondary winding to winding and winding to ground.

a. Minimum Test Voltage:  1000 V, dc.

b. Minimum Insulation Resistance:  500 megohms.

c. Duration of Each Test:  10 minutes.

d. Temperature Correction:  Correct results for test temperature deviation from 20 deg C standard.

E. Test Failures:  Compare test results with specified performance or manufacturer's data.  Correct deficiencies identified by tests and retest.  Verify that transformers meet specified requirements.

F. Report test results in writing.

3.3 ADJUSTING

A. Adjust transformer taps to provide optimum voltage conditions at utilization equipment throughout normal operating cycle of facility.  Record primary and secondary voltages and tap settings and submit with test results.

END OF SECTION 16461

DRY-TYPE TRANSFORMERS (1000 V AND LESS)
16461 - 1

