Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16715 - PREMISES TELEPHONE WIRING

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes premises wiring for telephone distribution, including installations for service by local telephone utility.

1.2 SUBMITTALS

A. Product Data:  For each type of telephone wiring component indicated.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction.

B. Comply with EIA/TIA 570.

C. Comply with NFPA 70.

1.4 COORDINATION

Delete below or edit to suit Project.  This Section assumes basic design coordination.

A. Coordinate premises wiring with requirements of [local telephone utility] [telephone equipment supplier].

PART 2 -  PRODUCTS

2.1 COMPONENTS

A. Telecommunications and Auxiliary Disconnect Outlets:  Four-position modular, latching, plug-type jack in flush-mounting wall plate, unless otherwise indicated.

B. Wall Plates:  Designed for telephone service.  Match those indicated for nearby power receptacle outlets for materials and finish.  For wall telephone units, include provision for support of unit.

No. 22 AWG conductors may be required for long cable runs.  Modify first paragraph below to suit Project or indicate conductor sizes on Drawings.

C. Distribution and Station Cable:  Comply with ICEA S-80-576.  Four-pair, No.  [24] [and] [22] AWG, solid-copper, unshielded, twisted-pair construction in PVC sheath.  In air-handling spaces use equivalent cable listed for use in plenums.

D. Cabinets:  Comply with Division 16 Section "Raceways and Boxes."  Furnish cabinets with backboard.

E. Backboard:  3/4-inch (19-mm) interior grade plywood.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Telephone Service:  Comply with local telephone utility's requirements for details of telephone service installation.

B. Install cable without damaging conductors and jacket.

1. Do not bend cable to a smaller radius than minimum recommended by manufacturer.

Edit first paragraph and subparagraphs below to specify wiring methods for premises wiring.

C. Wiring Method:  Install premises telephone wiring in accordance with the following:

1. Install cable in raceways, unless otherwise indicated.

2. Install cables without raceways in walls unless walls are solid or filled with insulation.  In solid walls, install in raceway[ and terminate raceway with a bushing in ceiling space above outlet].

3. Install cables without raceway where concealed in accessible ceiling space, unless otherwise indicated.

4. Use pulling methods that will not damage cable or raceway, including fish tape, cable, rope, and wire-cable grips.  Do not exceed manufacturer's recommended pulling tensions.

5. Conceal cable and raceway, except in unfinished spaces and as indicated.

D. Install exposed cable parallel or perpendicular to surfaces or exposed structural members and follow surface contours where possible.

1. Secure cable to independent supports at intervals as required to prevent sagging between supports.

Coordinate below with Drawings.

E. Backboard in Wire Closets: Cover entire wall up to 96 inches (2500 mm) above floor, unless otherwise indicated.

3.2 IDENTIFICATION

A. Identify components and circuits according to Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]."

B. Identify telephone system cabinets and backboards with the legend "Telephone."

C. Identify terminals at terminal strips, telecommunications outlets, and pull-and-junction boxes with approved designations.

3.3 FIELD QUALITY CONTROL

A. Testing:  Test continuity of each circuit pair loop.

END OF SECTION 16715

PREMISES TELEPHONE WIRING
16715 - 1

