Copyright 1996 AIA
MASTERSPEC
12/96


Copyright 1996, The American Institute of Architects (AIA)

SECTION 16722 - INTERCOMMUNICATION EQUIPMENT

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

Delete one of two paragraphs below to select type of system.

A. This Section includes direct-connected, manually switched, voice intercommunication equipment independent of telephone equipment.

B. This Section includes user-programmable, multichannel, microprocessor-switched, centrally controlled equipment, capable of expansion of up to 100 stations; and voice intercommunication equipment independent of telephone equipment.

1.3 PERFORMANCE REQUIREMENTS

Retain this Article for manually switched system.  Delete functions not required.

A. Master Station:  Capable of the following functions:

1. Communicating selectively with other master and speaker-microphone stations by operating selector switches.

2. Communicating simultaneously with all other stations by using a single all-call switch.

3. Conversing with individual stations in privacy.

4. Including other master-station connections in a multiple-station conference call.

5. Accessing separate paging speakers or groups of paging speakers by selector switches.

6. Overriding any conversation by a designated master station.

B. Speaker-Microphone Station:  Capable of the following functions:

Edit subparagraph below to reflect privacy features required.  Coordinate with Drawings.

1. Having privacy from remote monitoring without a warning tone signal at monitored station.  Designated speaker-microphone stations have a privacy switch to prevent another station from listening and to permit incoming calls.

2. Conversing hands free.

3. Calling master station by actuating call switch.

4. Returning a busy signal to indicate station is already in use.

C. Speakers:  Free from noise and distortion during operation and when in standby mode.

1.4 PERFORMANCE REQUIREMENTS

Retain this Article for user-programmable, microprocessor-switched system.  Delete functions not required.

A. Station Selection:  Capable of the following functions:

1. Communicating selectively with other master and speaker-microphone stations by dialing station's number on a 12-digit keypad.

2. Communicating simultaneously with all other stations by dialing a designated number on a 12-digit keypad.

3. Conversing with individual stations in privacy.

4. Including other master-station connections in a multiple-station conference call.

5. Accessing separate paging speakers or groups of paging speakers by dialing designated numbers on a 12-digit keypad.

6. Overriding any conversation by a designated master station.

7. Displaying selected station.

B. Speaker-Microphone Station:  Capable of the following functions:

Edit subparagraph below to reflect privacy features required.  Coordinate with Drawings.

1. Having privacy from remote monitoring without a warning tone signal at monitored station.  Designated speaker-microphone stations have a privacy switch to prevent another station from listening and to permit incoming calls.

2. Conversing hands free.

3. Calling master station by actuating call switch.

4. Returning a busy signal to indicate station is already in use.

C. Speakers:  Free from noise and distortion during operation and when in standby mode.

1.5 SUBMITTALS

A. Product Data:  For each component.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, required clearances, method of field assembly, components, and location of each field connection.

Delete subparagraphs below if not required.

Delete subparagraph below for systems with no built-in equipment.

1. Master-Station Details:  Scaled drawings for built-in equipment.

2. Wiring Diagrams:  Detail wiring for power, signal, and control systems and differentiate between manufacturer-installed and field-installed wiring.  Identify terminals to facilitate installation, operation, and maintenance.  Include a single-line diagram showing cabling interconnection of components.

C. Product Certificates:  Signed by manufacturers of equipment certifying that products furnished comply with specified requirements.

D. Installer Certificates:  Signed by manufacturer certifying that installers comply with requirements.

E. Manufacturer Certificates:  Signed by manufacturers certifying that they comply with requirements.

F. Field Test Reports:  Indicate and interpret test results for compliance with performance requirements.  Include record of final speaker-line matching transformer-tap settings, and signal ground-resistance measurement certified by Installer.

G. Maintenance Data:  For equipment to include in maintenance manuals specified in Division 1.

Delete below for manually switched equipment.

1. Include record of Owners equipment-programming option decisions.

1.6 QUALITY ASSURANCE

A. Installer Qualifications:  An experienced installer who is an authorized representative of equipment manufacturer for both installation and maintenance of equipment required for this Section.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction.

C. Comply with NFPA 70.

D. Comply with UL 50.

1.7 OCCUPANCY ADJUSTMENTS

Delete this Article if Owner contracts separately for this service.  Consider including a provision for submitting a continuing maintenance agreement proposal.

A. On-Site Assistance:  Engage a factory-authorized service representative to provide on-site assistance in adjusting sound levels, resetting transformer taps, and adjusting controls to meet occupancy conditions.  Provide up to three on-site assistance visits within one year of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.  Delete categories below not required for Project.

1. Aiphone Intercom Systems.

2. Alpha Communications.

3. Bogen Communications, Inc.

4. Dukane Corp.; Communications Systems Div.

5. Executone Information Systems Inc.

6. Federal Signal Corp.; Signal Div./Electrical Products.

7. Fisher Berkeley-Ektacom.

8. Jeron Electronic Systems Inc.

9. Rauland-Borg Corp.

10. Stentofon Communications, Inc.

11. 3-M Media InTouch.

12. TOA Electronics, Inc.

2.2 EQUIPMENT AND MATERIALS

A. Coordinate features to form an integrated system.  Match components and interconnections for optimum performance of specified functions.

Modify percentage in paragraph below to suit Project.

B. Expansion Capability:  Increase number of stations in the future by 25 percent above those indicated without adding any internal or external components or main trunk cable conductors.

C. Equipment:  Modular type using solid-state components, fully rated for continuous duty, unless otherwise indicated.  Select equipment for normal operation on input power usually supplied at 110 to 130 V, 60 Hz.

D. Waterproof Equipment:  Listed and labeled for duty outdoors or in damp locations.

Two Articles below cover products for alternative systems:  manually switched and microprocessor switched.  See Evaluations.  Delete system not used.  Delete features not required.  Add other project-required features.

2.3 MASTER STATIONS

This Article is for manually switched system.  Revise to suit Project.

A. Station-Selector and Talk-Listen Switches:  Heavy-duty type with gold-plated contacts rated for five million operations.

B. Volume Control:  Regulates incoming-call volume.

C. Light Annunciation:  Identifies calling stations and stations in use.  Light remains on until call is answered.

D. Tone Annunciation:  Momentary audible tone signal announces incoming calls.

E. Speaker Microphone:  Transmits and receives calls.

1. Minimum Speaker Sensitivity:  EIA pressure rating of 40 dB.

F. Handset with Hook Switch:  Telephone type with 18-inch- (450-mm-) long, permanently coiled cord.  Arrange to disconnect speaker when handset is lifted.

G. Central-Control Cabinet:  Comply with EIA-310-D.  Lockable, ventilated metal cabinet houses terminal strips, power supplies, amplifiers, system volume control, and auxiliary equipment.

2.4 MASTER STATIONS

This Article is for microprocessor-switched system.  Revise to suit Project.

A. Twelve-Digit Keypad Selector:  Transmits calls to other stations and initiates commands for programming and operation.

B. Volume Control:  Regulates incoming-call volume.

C. Light Annunciation:  Identifies calling stations and stations in use.  Light remains on until call is answered.

D. Tone Annunciation:  Momentary audible tone signal announces incoming calls.

E. Speaker Microphone:  Transmits and receives calls.

1. Minimum Speaker Sensitivity:  EIA pressure rating of 40 dB.

F. Handset with Hook Switch:  Telephone type with 18-inch- (450-mm-) long, permanently coiled cord.  Arrange to disconnect speaker when handset is lifted.

G. Reset Control:  Cancels call and resets system for next call.

H. Central-Control Cabinet:  Comply with EIA-310-D.  Lockable, ventilated metal cabinet houses terminal strips, power supplies, amplifiers, system volume control, and other switching and control devices required for conversation channels and control functions.

2.5 SPEAKER-MICROPHONE STATIONS

System components in this Article are common to both manually and microprocessor-switched systems.  Delete products not required.  Modify remaining ones and add others as needed.

A. Mounting:  Flush, unless otherwise indicated, and suitable for mounting conditions indicated.

B. Faceplate:  Stainless steel or anodized aluminum with tamperproof mounting screws.

C. Back Box:  Two-gang galvanized steel with 2-1/2-inch (64-mm) minimum depth.

D. Speaker:  Comply with EIA SE-103.  3-inch (76-mm), 2.3-oz. (65-g) minimum, permanent magnet.

E. Recurring momentary tone announces incoming call.

F. Call Switch:  Mount on faceplate.  Permits a call to master station.

G. Privacy Switch:  Mount on faceplate.  When in on position, switch prevents transmission of sound from remote station to system; when in off position, without further switch manipulation, response can be made to incoming calls.

H. Handset with Hook Switch:  Telephone type with 18-inch- (450-mm-) long, permanently coiled cord.  Arrange to disconnect speaker when handset is lifted.

2.6 CALL-SWITCH UNIT

A. Enclosure:  Single-gang box with a stainless-steel faceplate.

B. Call Switch:  Momentary contact signals system that a call has been placed.

C. Privacy Switch:  Prevents transmission of sound signals from station to system.

D. Volume Control:  Operated by screwdriver blade through a hole in faceplate to adjust output level of associated speaker.

E. Handset with Hook Switch:  Telephone type with 18-inch- (450-mm-) long, permanently coiled cord.  Arrange to disconnect speaker when handset is lifted.

2.7 ALL-CALL AMPLIFIER

Delete this Article if all-call feature is not required.  Coordinate with system functional performance description.

A. Comply with EIA SE-101-A.

B. Output Power:  At least 0.5 W, RMS for each station and speaker connected in all-call mode of operation, plus an allowance for future stations.

C. Total Harmonic Distortion:  Less than 5 percent at rated output power with a load equivalent to quantity of stations connected in all-call mode of operation.

D. Minimum Signal-to-Noise Ratio:  45 dB, at rated output.

E. Frequency Response:  Within plus or minus 3 dB from 70 to 12,000 Hz.

F. Output Regulation:  Maintains output level within 2 dB from full to no load.

G. Input Sensitivity:  Compatible with master stations and central equipment so amplifier delivers full-rated output with a sound-pressure level of less than 10 dynes/sq. cm impinging on a master station, speaker microphone, or handset transmitter.

H. Amplifier Protection:  Prevents damage from shorted or open output.

2.8 INTERCOMMUNICATION AMPLIFIER

A. Comply with EIA SE-101-A.

B. Minimum Output Power:  2 W, RMS and adequate for all functions.

C. Total Harmonic Distortion:  Less than 5 percent at rated output power with a load equivalent to one station connected to output terminals.

D. Minimum Signal-to-Noise Ratio:  45 dB, at rated output.

E. Frequency Response:  Within plus or minus 3 dB from 70 to 10,000 Hz.

F. Output Regulation:  Maintains output level within 2 dB from full to no load.

G. Input Sensitivity:  Compatible with speaker microphones in master stations and speaker-microphone stations so amplifier delivers full-rated output with a sound-pressure level of not more than 10 dynes/sq. cm impinging on a master station, speaker microphone, or handset transmitter.

H. Amplifier Protection:  Prevents damage from shorted or open output.

2.9 PAGING AMPLIFIER

Delete this Article if Project does not require paging over speakers separate from those associated with intercom stations.  Delete if paging amplification is provided by a separate public address system.

A. Comply with EIA SE-101-A.

B. Input Voltage:  120-V ac, 60 Hz.

C. Frequency Response:  Within plus or minus 3 dB from 60 to 10,000 Hz.

D. Minimum Signal-to-Noise Ratio:  60 dB, at rated output.

E. Total Harmonic Distortion:  Less than 3 percent at rated power output from 70 to 12,000 Hz.

F. Output Regulation:  Less than 2 dB from full to no load.

G. Controls:  On/off, input levels, and low-cut filter.

H. Input Sensitivity:  Matched to input circuit and providing full-rated output with a sound-pressure level of less than 10 dynes/sq. cm impinging on a speaker microphone or handset transmitter.

I. Amplifier Protection:  Prevents damage from shorted or open output.

J. Output Circuit:  70-W line.

2.10 CONE-TYPE LOUDSPEAKERS/SPEAKER MICROPHONES

A. Comply with EIA SE-103.

B. Minimum Axial Sensitivity:  EIA pressure rating of 45 dB.

C. Frequency Response:  Within plus or minus 3 dB from 70 to 15,000 Hz.

D. Minimum Dispersion Angle:  100 degrees.

E. Line Transformer:  Comply with EIA-160, maximum insertion loss of 0.5 dB, power rating equal to speaker's, and at least four level taps.

F. Enclosures:  Steel housings or back boxes, acoustically dampened, with front face of at least 0.0478-inch (1.2-mm) steel and whole assembly rust proofed and factory primed; suitable for surface ceiling, flush ceiling, pendant or wall mounting as indicated.

Revise paragraph below to suit architectural requirements.

G. Baffle:  For flush speakers, provide a speaker baffle of at least 0.032-inch (0.8-mm) aluminum, brushed to a satin sheen and lacquered.

H. Size:  8 inches (200 mm) with 1-inch (25-mm) voice coil and minimum 5-oz. (140-g) ceramic magnet.

2.11 HORN-TYPE LOUDSPEAKERS/SPEAKER MICROPHONES

A. Comply with EIA SE-101-A.  All-metal, weatherproof construction.  Complete with universal mounting brackets.

B. Frequency Response:  Within plus or minus 3 dB from 275 to 14,000 Hz.

C. Minimum Power Rating of Driver:  15 W, continuous.

D. Minimum Dispersion Angle:  110 degrees.

E. Line Transformer:  Comply with EIA-160, maximum insertion loss of 0.5 dB, power rating equal to speaker's, and at least four volume taps.

2.12 CONDUCTORS AND CABLES

A. Conductors:  Jacketed single and multitwisted pair, untinned solid copper.  Sizes as recommended by system manufacturer, but not smaller than No. 22 AWG.

B. Insulation:  Thermoplastic, not less than 1/32 inch (0.8 mm) thick.

C. Shielding:  For speaker-microphone leads and elsewhere where recommended by manufacturer; No. 34 AWG tinned, soft-copper strands formed into a braid or equivalent foil.

1. Minimum Shielding Coverage on Conductors:  60 percent.

D. Plenum Cable:  Listed and labeled for plenum installation.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install equipment to comply with manufacturer's written instructions.

B. Wiring Method:  Install wiring in raceway except within consoles, desks, and counters.  Conceal cable and raceway except in unfinished spaces.

Select paragraph above or below.

C. Wiring Method:  Install wiring in raceway except within consoles, cabinets, desks, and counters and except in accessible ceiling spaces and in gypsum-board partitions where cable wiring method may be used.  Use plenum cable in environmental air spaces, including plenum ceilings.  Conceal cable and raceway except in unfinished spaces.

Modify paragraphs below to suit Project.

D. Install exposed cables parallel and perpendicular to surfaces or exposed structural members, and follow surface contours.  Secure and support cables by straps, staples, or similar fittings designed and installed to avoid damage to cables.  Secure cable at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, or fittings.

E. Wiring within Enclosures:  Bundle, lace, and train conductors to terminal points with no excess.  Use lacing bars in cabinets.

F. Control-Circuit Wiring:  Install number and size of conductors as recommended by system manufacturer for control functions indicated.

G. Separation of Wires:  Separate speaker-microphone, line-level, speaker-level, and power wiring runs.  Install in separate raceways or, where exposed or in same enclosure, separate conductors at least 12 inches (300 mm) for speaker microphones and adjacent parallel power and telephone wiring.  Separate other intercommunication equipment conductors as recommended by equipment manufacturer.

H. Splices, Taps, and Terminations:  Make splices, taps, and terminations on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

I. Match input and output impedances and signal levels at signal interfaces.  Provide matching networks where required.

J. Identification of Conductors and Cables:  Color-code conductors and apply wire and cable marking tape to designate wires and cables to identify media in coordination with system wiring diagrams.

K. Cut and patch existing walls, ceilings, floors, or other building finishes for installation.  Repair, restore, and refinish surfaces to original appearance.

3.2 GROUNDING

Revise this Article to suit system requirements.  Include grounding electrodes for special applications only.

A. Ground cable shields and equipment to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.

B. Signal Ground Terminal:  Locate at main equipment cabinet.  Isolate from power system and equipment grounding.

C. Install grounding electrodes as specified in Division 16 Section "Grounding."

3.3 FIELD QUALITY CONTROL

Select one of two paragraphs below.  First is for manually switched system.  Second is for microprocessor-switched system.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect field-assembled components and equipment installations, including connections.  Report results in writing.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect field-assembled components and equipment installations, including connections and initial system programming.  Report results in writing.

Delete paragraph below for manually switched systems.

C. Programming:  Fully brief Owner on available programming options.  Record Owners decisions and set up initial system program.  Prepare a written record of decisions, implementation methodology, and final results.

Modify test requirements in paragraphs below where all-call or paging are not specified.

D. Operational Test:  Test originating station-to-station, all-call, and page messages at each intercommunication station.  Verify proper routing and volume levels and freedom from noise and distortion.  Test each available message path from each station on system.

E. Frequency Response Test:  Determine frequency response of two transmission paths, including all-call and paging by transmitting and recording audio tones.  Minimum acceptable performance is within 3 dB from 150 to 2500 Hz.

F. Signal-to-Noise Ratio Test:  Measure the ratio of signal to noise of complete system at normal gain settings, using the following procedure:

1. Disconnect a speaker microphone and replace it in the circuit with a signal generator using a 1000-Hz signal.  Measure the ratio of signal to noise at paging speakers.

2. Repeat test for four speaker microphones and for each separately controlled zone of paging loudspeakers.

3. Minimum acceptable ratio is 35 dB.

G. Distortion Test:  Measure distortion at normal gain settings and rated power.  Feed signals at frequencies of 150, 200, 400, 1000, and 2500 Hz into each paging and all-call amplifier, and a minimum of two selected intercommunication amplifiers.  For each frequency, measure the distortion in the paging and all-call amplifier outputs.  Maximum acceptable distortion at any frequency is 5 percent total harmonics.

H. Acoustic Coverage Test:  Feed pink noise into system using octaves centered at 500 and 4000 Hz.  Use a sound-level meter with octave-band filters to measure level at three locations in each paging zone.  Maximum permissible variation in level is plus or minus 3 dB, and in levels between adjacent zones is plus or minus 5 dB.

Delete paragraph below if paging is not specified.

I. Power Output Test:  Measure electrical power output of each paging amplifier at normal gain setting at 150, 1000, and 2500 Hz.  Maximum variation in power output at these frequencies is plus or minus 3 dB.

J. Signal Ground Test:  Measure and report ground resistance at system signal ground.  Comply with testing requirements in Division 16 Section "Grounding."

K. Retesting:  Correct deficiencies and retest.  Prepare written record of tests.

L. Inspection:  Verify that units and controls are properly labeled and interconnecting wires and terminals are identified.  Prepare a list of final tap settings of paging speaker-line matching transformers.

M. Schedule tests with at least seven days advance notice of test performance.

3.4 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain equipment as specified below:

Delete subparagraph below for manually switched equipment.

1. Train Owners maintenance personnel on programming equipment for starting up and shutting down, troubleshooting, servicing, and maintaining equipment.

2. Review data in maintenance manuals.  Refer to Division 1 Section "Contract Closeout."

Delete subparagraph above or below depending on which Section is retained in Division 1.

3. Review data in maintenance manuals.  Refer to Division 1 Section "Operation and Maintenance Data."

4. Schedule training with Owner, through Architect, with at least seven days' advance notice.

END OF SECTION 16722

INTERCOMMUNICATION EQUIPMENT
16722 - 1

