Copyright 1996 AIA
MASTERSPEC
12/96


Copyright 1996, The American Institute of Architects (AIA)

SECTION 16726 - PUBLIC ADDRESS AND MUSIC EQUIPMENT

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes equipment for amplifying, distributing, and reproducing sound signals.

1.3 DEFINITIONS

A. Channels:  Separate parallel signal paths, from sources to loudspeakers or loudspeaker zones, with separate amplification and switching that permit selection between paths for speaker alternative program signals.

B. Zone:  A separate group of loudspeakers and associated supply wiring that may be arranged for selective switching between different channels.

Retain abbreviations that remain after this Section has been edited for Project.

C. VU:  Volume unit.

1.4 PERFORMANCE REQUIREMENTS

Descriptions below are offered as examples only.  This Article provides the place to convey design intent to Contractor and Installer.  Revise to suit Project.

A. System Functions:  Include the following:

Select functions from subparagraphs below.  Delete those not required and adjust descriptions to suit Project.  Add other functions as required.

1. Selectively connecting separate zones to different signal channels.

2. Selectively amplifying sound among various microphone outlets and other inputs.

3. Communicating simultaneously to all zones regardless of zone or channel switch settings.

4. Paging, by dialing an extension from any local telephone instrument and speaking into the telephone.

5. Producing a program-signal tone that is amplified and sounded over all speakers, overriding signals currently being distributed.

6. Reproducing high-quality sound that is free from noise and distortion at all loudspeakers at all times during equipment operation, including standby mode with inputs off; and output free from nonuniform coverage of amplified sound.

1.5 SUBMITTALS

A. Product Data:  For each type of equipment.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, required clearances, method of field assembly, components, and location of each field connection.

Delete subparagraphs below if not required.

1. Console layouts.

2. Control panels.

3. Rack arrangements.

4. Wiring Diagrams:  Detail wiring for power, signal, and control systems and differentiate between manufacturer-installed and field-installed wiring.  Identify terminals to facilitate installation, operation, and maintenance.  Include a single-line diagram showing cabling interconnection of components.

C. Calculations:  For sizing backup battery.

D. Product Certificates:  Signed by manufacturers of equipment certifying that products furnished comply with specified requirements.

E. Installer Certificates:  Signed by manufacturer certifying that installers comply with requirements.

F. Manufacturer Certificates:  Signed by manufacturers certifying that they comply with requirements.

G. Field Test Reports:  Indicate and interpret test results for compliance with performance requirements.  Include record of final speaker-line matching transformer-tap settings, and signal ground-resistance measurement certified by Installer.

H. Maintenance Data:  For equipment to include in maintenance manuals specified in Division 1.

1.6 QUALITY ASSURANCE

A. Installer Qualifications:  An experienced installer who is an authorized representative of equipment manufacturer for both installation and maintenance of equipment required for this Section.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction.

C. Comply with NFPA 70.

D. Comply with UL 50.

1.7 OCCUPANCY ADJUSTMENTS

Delete this Article if Owner contracts separately for this service.  Consider including a provision for submitting a continuing maintenance agreement proposal.

A. On-Site Assistance:  Engage a factory-authorized service representative to provide on-site assistance in adjusting sound levels, resetting transformer taps, and adjusting controls to meet occupancy conditions.  Provide up to three on-site assistance visits within one year of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.  Delete categories below not required for Project.

1. Alpha Communications.

2. Altec Lansing/University Sound.

3. Atlas-Soundolier; Atapco Security & Communications Group.

4. Bogen Communications, Inc.

5. Dukane Corp.; Communications Systems Div.

6. Electro-Voice, Inc.

7. Executone Information Systems Inc.

8. Federal Signal Corp.; Signal Div./Electrical Products.

9. Peavey Electronics Corp.

10. Rauland-Borg Corp.

11. Whelen Engineering Co., Inc.

2.2 EQUIPMENT

A. Coordinate features to form an integrated system.  Match components and interconnections for optimum performance of specified functions.

B. Equipment:  Modular type, using solid-state components, fully rated for continuous duty, unless otherwise indicated.  Select equipment for normal operation on input power usually supplied at 110 to 130 V, 60 Hz.

C. Waterproof Equipment:  Listed and labeled for duty outdoors or in damp locations.

2.3 PREAMPLIFIERS

A. Comply with EIA SE-101-A; either separately mounted or as an integral part of power amplifier.

B. Output Power:  Plus 4 dB above 1 mW at matched power-amplifier load.

C. Total Harmonic Distortion:  Less than 1 percent.

D. Frequency Response:  Within plus or minus 2 dB from 20 to 20,000 Hz.

E. Input Jacks:  Minimum of two.  One matched for low-impedance microphone; the other matchable to cassette deck, CD player, or radio tuner signals without external adapters.

F. Minimum Noise Level:  Minus 55 dB below rated output.

G. Controls:  On/off, input levels, and master gain.

2.4 POWER AMPLIFIERS

A. Comply with EIA SE-101-A.

Revise paragraph below to suit Project.

B. Mounting:  Rack mounted.

C. Output Power:  70-W balanced line.

D. Frequency Response:  Within plus or minus 2 dB from 50 to 12,000 Hz.

E. Minimum Signal-to-Noise Ratio:  60 dB, at rated output.

F. Total Harmonic Distortion:  Less than 3 percent at rated power output from 50 to 12,000 Hz.

G. Output Regulation:  Less than 2 dB from full to no load.

H. Controls:  On/off, input levels, and low-cut filter.

I. Input Sensitivity:  Matched to preamplifier and providing full-rated output with a sound-pressure level of less than 10 dynes/sq. cm impinging on a speaker microphone or handset transmitter.

2.5 TRANSFER TO STANDBY AMPLIFIER

Delete this Article, except for applications where continuity of service is required regardless of amplifier failure.  Coordinate with Drawings.

A. Monitoring Circuit and Sensing Relay:  Arranged to detect reduction in output of power amplifier of 40 percent or greater and, in such event, transfer load and signal automatically to standby amplifier.

2.6 COMPONENTS

A. Microphone:  Comply with EIA SE-105.

1. Type:  Dynamic, with cardioid polar or omnidirectional characteristic.

2. Impedance:  150 ohms.

3. Frequency Response:  Uniform, 60 to 12,000 Hz.

4. Output Level:  Minus 58 dB minimum.

5. Finish:  Satin chrome.

6. Mounting:  Desk stand with integral-locking, press-to-talk switch.

Since microphones are portable items that can be plugged into any microphone outlet, retain subparagraph below to specify quantities.  See Evaluations.

7. Quantity of Microphones:  Four, including one spare.

8. Quantity of Desk Stands:  Three.

Delete paragraph and subparagraphs below for small, simple systems.

B. Volume Limiter/Compressor:  Equip each zone with a volume limiter/compressor.  Install in central equipment cabinet.  Arrange to provide a constant input to power amplifiers.

1. Frequency Response:  45 to 15,000 Hz, plus or minus 1 dB minimum.

2. Signal Reduction Ratio:  At least a 10:1 and 5:1 selectable capability.

3. Distortion:  1 percent, maximum.

4. Rated Output:  Minimum of plus 14 dB.

5. Inputs:  Minimum of two inputs with variable front-panel gain controls and a VU or dB meter for input adjustment.

Delete paragraph and subparagraphs below if not required or revise to suit Project.  Console can vary from a small switch and pilot-light panel to a large, complex unit.  Coordinate with Drawings for identification of items to be mounted and for console mounting provision:  desk, counter, wall, etc.

C. Control Console:  Modular, desktop cabinet; complying with EIA-310.

1. Housing:  Steel, 0.0478 inch (1.2 mm) minimum, with removable front and rear panels.  Side panels are removable for interconnecting side-by-side mounting.

2. Panel for Equipment and Controls:  Each module is nominal 19 inches (483 mm) wide by 8-3/4 inches (222 mm) high.

3. Controls:  Include the following:

a. Switching devices to select signal sources for distribution channels.

b. Program selector switch to select source for each program channel.

c. Switching devices to select zones for paging.

d. All-call selector switch.

4. Indicators:  A visual annunciation for each distribution channel to indicate source being used.

Include subparagraph below for consoles using self-contained power and control units with integral power amplifiers.  (Amplifiers available with up to 40-W rating.)

5. Self-Contained Power and Control Unit:  A single assembly of basic control, electronics, and power supply necessary to accomplish specified functions.

6. Spare Positions:  20 percent spare zone control and annunciation positions on console.

7. Microphone jack.

Delete paragraph and subparagraphs below if not required.  Paging access from intercommunication equipment may be similarly specified.

D. Telephone Paging Adapter:  Arranged to accept voice signals from telephone extension dialing access and to automatically provide amplifier input and program override for preselected zones.

1. Minimum Frequency Response:  Flat, 200 to 2500 Hz.

2. Impedance Matching:  Adapter matches telephone line to public address equipment input.

E. Tone Generator:  For clock and program interface.

1. Signals Produced:  Minimum of seven distinct, audible signal types, including wail, warble, high/low, alarm, repeating chimes, single-stroke chime, and tone.

2. Pitch Control:  Chimes and tone.

3. Volume Control:  All outputs.

4. Activation-Switch Network:  Establishes priority and hierarchy of output signals produced by different activation setups.

Delete one or both types of equipment housing below.

F. Equipment Cabinet:  Comply with EIA-310-D.  House amplifiers and auxiliary equipment at each location.

Delete rear-locking doors in subparagraph below if no rear access.

1. Cabinet Housing:  Construct of 0.0478-inch (1.2-mm) steel, minimum, with front- and rear-locking doors and standard EIA 19-inch (483-mm) racks.  Arrange for floor or wall mounting as indicated.  Size to house all equipment indicated plus spare capacity.  Include 20 percent minimum spare capacity for future equipment over and above space required for future cassette deck and CD player.

2. Power Provisions:  Install a single switch in cabinet to supply cabinet power distribution system and electrical outlets, uniformly spaced, to accommodate ac-power cords of each item of equipment.

3. Ventilation:  A low-noise fan for forced-air cabinet ventilation.  Equip fan with a filtered input vent and connect to operate from 105- to 130-V ac, 60 Hz; separately fused and switchable and arranged to be powered when main cabinet power switch is on.

G. Equipment Rack:  Comply with EIA-310-D.  House amplifiers and auxiliary equipment in standard EIA 19-inch (483-mm) racks.

1. Group items of same function together, either vertically or side by side, and arrange controls symmetrically.

2. Power-Supply Connections:  Approved plugs and receptacles.

3. Arrange all inputs, outputs, interconnections, and test points so they are accessible at rear of rack for maintenance and testing, with each item removable from rack without disturbing other items or connections.

4. Blank Panels:  Cover empty space in equipment racks so entire front of rack is occupied by panels.

5. Enclosure Panels:  Ventilated rear and sides and solid top.  Use louvers in panels to ensure adequate ventilation.

6. Finish:  Uniform, baked-enamel factory finish over rust-inhibiting primer.

7. Power-Control Panel:  On front of equipment housing, with a master power on/off switch and pilot light, and socket for a 5-A, indicating, cartridge fuse for rack equipment power.

8. Service Light:  At top rear of rack and control by an adjacent switch.

9. Vertical Plug Strip:  Grounded receptacles, 12 inches (300 mm) o.c. the full height of rack, to supply rack-mounted equipment.

10. Maintenance Receptacles:  Duplex convenience outlets supplied independent of equipment plug strip and located in front and bottom rear of rack.

Revise percent in subparagraph below to suit Project.

11. Spare Capacity:  20 percent spare space capacity in rack for future equipment.

H. Monitor Panel:  A monitor panel mounted above amplifiers.

1. Equip with a VU or dB meter, a speaker with volume control, and a multiple-position rotary selector switch.

2. Connect selector switch and volume control to permit selective monitoring of output of each separate power amplifier via a VU or dB meter and speaker.

Coordinate paragraph and subparagraphs below with Drawings.

I. Cone-Type Loudspeakers:  Comply with EIA SE-103.

1. Minimum Axial Sensitivity:  EIA pressure rating of 45 dB.

2. Frequency Response:  Within plus or minus 3 dB from 50 to 15,000 Hz.

3. Size:  8 inches (200 mm) with 1-inch (25-mm) voice coil and minimum 5-oz. (140-g) ceramic magnet.

4. Minimum Dispersion Angle:  100 degrees.

5. Rated Output Level:  10 W.

6. Matching Transformer:  Comply with EIA-160.  Full-power rated with four EIA standard taps.  Maximum insertion loss of 0.5 dB.

Coordinate subparagraph below with Drawings.

7. Surface-Mounting Units:  Ceiling, wall, or pendant mounting, as indicated, in steel back boxes, acoustically dampened.  Front face of at least 0.0478-inch (1.2-mm) steel and whole assembly rust proofed and shop primed for field painting.

Modify finish description below as required to suit aesthetic requirements.

8. Flush-Ceiling Mounting Units:  In steel back boxes, acoustically dampened.  Metal ceiling grille with baked, white-enamel finish.

Device below is specified as a sample.  Revise as required to suit Project and manufacturer's standard equipment.  Coordinate with Drawings.

J. Horn-Type Loudspeakers:  Comply with EIA SE-103.

1. Type:  Single-horn units, double-reentrant design, with minimum full-range power rating of 15 W.

2. Matching Transformer:  Comply with EIA-160.  Full-power rated with four EIA standard taps.  Maximum insertion loss of 0.5 dB.

3. Frequency Response:  Within plus or minus 3 dB from 250 to 12,000 Hz.

4. Dispersion Angle:  130 by 110 degrees.

5. Mounting:  Integral bracket.

6. Units in Hazardous (Classified) Locations:  Listed and labeled for the environment in which they are located.

Delete paragraph and subparagraphs below except for large spaces where ambient noise level in space varies greatly under different use conditions and manual level adjustment is impractical, i.e., in some cafeterias.

K. Noise-Operated Gain Controller:  Units continuously sense space noise level and automatically adjust signal level to local speakers.

1. Frequency Response:  20 to 20,000 Hz, plus or minus 1 dB.

2. Level Adjustment Range:  20 dB minimum.

3. Maximum Distortion:  1 percent.

4. Control:  Permits adjustment of sensing level of device.

Delete paragraph and subparagraphs below where volume attenuator stations are not used.

L. Volume Attenuator Stations:  Wall-plate-mounted autotransformer type with paging priority feature.

1. Wattage Rating:  10 W, unless otherwise indicated.

2. Attenuation per Step:  3 dB, with positive off position.

3. Insertion Loss:  0.4 dB maximum.

4. Attenuation Bypass Relay:  Single pole, double throw.  Connected to operate and bypass attenuation when all-call, paging, program signal, or prerecorded message features are used.  Relay returns to normal position at end of priority transmission.

5. Label:  "PA Volume."

Edit two paragraphs below to suit Project.

M. Microphone Outlets:  Three-pole, polarized, locking-type, microphone receptacles in single-gang boxes.  Equip wall outlets with a brushed stainless-steel device plate.  Equip floor outlets with gray tapered rubber or plastic cable nozzles and fixed outlet covers.

Delete paragraph below unless system operates during a power outage.

N. Headphone Outlets (for Hearing Impaired):  Microphone receptacles in single-gang boxes.  Equip wall outlets with a brushed stainless-steel device plate.  Equip floor outlets with gray tapered rubber or plastic cable nozzles and fixed outlet covers.

O. Battery Backup Power Unit:  Rack-mounted unit consisting of time-delay relay, sealed lead-calcium battery, battery charger, on/off switch and "normal" and "emergency" indicating lights, and adequate capacity to supply maximum equipment power requirements for one hour of continuous full operation.

1. Arrange unit to supply public address equipment with 12- to 15-V dc power automatically during an outage of normal 120-V ac power.

2. Arrange for battery to be on float charge when not supplying system and to transfer automatically to supply system after three to five seconds of continuous outage of normal power, as sensed by time-delay relay.

3. Automatic retransfer of system to normal supply when normal power has been reestablished for three to five seconds continuously.

P. Cable and Conductors:  Jacketed, twisted-pair and twisted-multipair, untinned, solid-copper conductors.

1. Insulation for Wire in Conduit:  Thermoplastic, not less than 1/32 inch (0.8 mm) thick.

2. Microphone Cables:  Neoprene jacketed, not less than 2/64 inch (0.8 mm) thick over shield with filled interstices.  Shield No. 34 AWG tinned, soft-copper strands formed into a braid or approved equivalent foil.  Shielding coverage on conductors is not less than 60 percent.

3. Plenum Cable:  Listed and labeled for plenum installation.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install equipment to comply with manufacturer's written instructions.

B. Wiring Method:  Install wiring in raceway except within consoles, desks, and counters.  Conceal cable and raceway except in unfinished spaces.

Select paragraph above or below.

C. Wiring Method:  Install wiring in raceway except within consoles, cabinets, desks, and counters and except in accessible ceiling spaces and in gypsum-board partitions where cable wiring method may be used.  Use plenum cable in environmental air spaces, including plenum ceilings.  Conceal cable and raceway except in unfinished spaces.

Modify paragraphs below to suit Project.

D. Install exposed cables parallel and perpendicular to surfaces or exposed structural members, and follow surface contours.  Secure and support cables by straps, staples, or similar fittings so designed and installed to avoid damage to cables.  Secure cable at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, or fittings.

E. Wiring within Enclosures:  Bundle, lace, and train conductors to terminal points with no excess.  Use lacing bars in cabinets.

F. Control-Circuit Wiring:  Install number and size of conductors as recommended by system manufacturer for control functions indicated.

G. Separation of Wires:  Separate speaker-microphone, line-level, speaker-level, and power wiring runs.  Install in separate raceways or, where exposed or in same enclosure, separate conductors at least 12 inches (300 mm) for speaker microphones and adjacent parallel power and telephone wiring.  Separate other intercommunication equipment conductors as recommended by equipment manufacturer.

H. Splices, Taps, and Terminations:  Make splices, taps, and terminations on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

I. Match input and output impedances and signal levels at signal interfaces.  Provide matching networks where required.

J. Identification of Conductors and Cables:  Color-code conductors and apply wire and cable marking tape to designate wires and cables to identify media in coordination with system wiring diagrams.

K. Wall-Mounting Outlets:  Flush mounted.

L. Floor-Mounting Outlets:  Conceal in floor and install cable nozzles through outlet covers.  Secure outlet covers in place.  Trim with carpet in carpeted areas.

M. Conductor Sizing:  Unless otherwise indicated, size speaker circuit conductors from racks to loudspeaker outlets not smaller than No. 18 AWG and conductors from microphone receptacles to amplifiers not smaller than No. 22 AWG.

N. Weatherproof Equipment:  Install units that are mounted outdoors,  in damp locations, or where exposed to weather consistent with requirements of weatherproof rating.

O. Line Matching Transformer Connections:  Make initial connections using tap settings indicated on Drawings.

3.2 GROUNDING

Revise this Article to suit system requirements.  Include grounding electrodes for special applications only.

A. Ground cable shields and equipment to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.

B. Signal Ground Terminal:  Locate at main equipment cabinet.  Isolate from power system and equipment grounding.

C. Install grounding electrodes as specified in Division 16 Section "Grounding."

3.3 FIELD QUALITY CONTROL

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect field-assembled components and equipment installations, including connections.  Report results in writing.

B. Operational Test:  Perform tests that include originating program and page material at microphone outlets, preamplifier program inputs, and other inputs.  Verify proper routing and volume levels and freedom from noise and distortion.

C. Signal-to-Noise Ratio Test:  Measure the ratio of signal to noise of complete system at normal gain settings, using the following procedure:

1. Disconnect a microphone at the connector or jack closest to it and replace it in the circuit with a signal generator using a 1000-Hz signal.  Replace all other microphones at corresponding connectors with dummy loads, each equal in impedance to microphone it replaces.  Measure the ratio of signal to noise.

2. Repeat test for each separately controlled zone of loudspeakers.

3. Minimum acceptance ratio is 50 dB.

D. Distortion Test:  Measure distortion at normal gain settings and rated power.  Feed signals at frequencies of 50, 200, 400, 1000, 3000, 8000, and 12,000 Hz into each preamplifier channel.  For each frequency, measure the distortion in the paging and all-call amplifier outputs.  Maximum acceptable distortion at any frequency is 3 percent total harmonics.

E. Acoustic Coverage Test:  Feed pink noise into system using octaves centered at 500 and 4000 Hz.  Use a sound-level meter with octave-band filters to measure level at five locations in each zone.  For spaces with seated audiences, maximum permissible variation in level is plus or minus 2 dB.  In addition, the levels between locations in the same zone and between locations in adjacent zones must not vary more than plus or minus 3 dB.

F. Power Output Test:  Measure electrical power output of each power amplifier at normal gain setting at 50, 1000, and 12,000 Hz.  Maximum variation in power output at these frequencies must not exceed plus or minus 1 dB.

G. Signal Ground Test:  Measure and report ground resistance at pubic address equipment signal ground.  Comply with testing requirements specified in Division 16 Section "Grounding."

H. Retesting:  Correct deficiencies, revising tap settings of speaker-line matching transformers where necessary to optimize volume and uniformity of sound levels, and retest.  Prepare written record tests.

I. Inspection:  Verify that units and controls are properly labeled and interconnecting wires and terminals are identified.  Prepare a list of final tap settings of paging speaker-line matching transformers.

J. Schedule tests with at least seven days' advance notice of test performance.

3.4 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain equipment as specified below:

Delete subparagraph below for manually switched equipment.

1. Train Owners maintenance personnel on programming equipment for starting up and shutting down, troubleshooting, servicing, and maintaining equipment.

2. Review data in maintenance manuals.  Refer to Division 1 Section "Contract Closeout."

Delete subparagraph above or below depending on which Section is retained in Division 1.

3. Review data in maintenance manuals.  Refer to Division 1 Section "Operation and Maintenance Data."

4. Schedule training with Owner, through Architect, with at least seven days' advance notice.

END OF SECTION 16726

PUBLIC ADDRESS AND MUSIC EQUIPMENT
16726 - 1

