Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16726 - PUBLIC ADDRESS AND MUSIC EQUIPMENT

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes equipment for amplifying, distributing, and reproducing sound signals.

1.2 PERFORMANCE REQUIREMENTS

Descriptions below are offered as examples only.  This Article provides the place to convey design intent to Contractor and Installer.  Revise to suit Project.

A. System Functions:  Include the following:

Select functions from subparagraphs below.  Delete those not required and adjust descriptions to suit Project.  Add other functions as required.

1. Selectively amplifying sound signals from various microphone outlets and other inputs.

2. Paging, by dialing an extension from any local telephone instrument and speaking into the telephone.

3. Reproducing high-quality sound that is uniformly distributed and free from noise and distortion at all loudspeakers at all times during equipment operation, including standby mode with inputs off.

1.3 SUBMITTALS

A. Product Data:  For each type of public address and music equipment component indicated.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, required clearances, method of field assembly, components, and location of each field connection.

Delete subparagraphs below if not required.

1. Rack arrangements.

2. Wiring Diagrams:  Power, signal, and control wiring.

C. Installer certificates.

D. Field quality-control test reports.

E. Operation and maintenance data.

1.4 QUALITY ASSURANCE

A. Installer Qualifications:  A qualified installer, approved by manufacturer to install manufacturer's products.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Alpha Communications.

2. Altec Lansing/University Sound.

3. Atlas-Soundolier; Atapco Security & Communications Group.

4. Bogen Communications, Inc.

5. Dukane Corp.; Communications Systems Div.

6. Electro-Voice, Inc.

7. Executone Information Systems Inc.

8. Federal Signal Corp.; Signal Div./Electrical Products.

9. Peavey Electronics Corp.

10. Rauland-Borg Corp.

11. Whelen Engineering Co., Inc.

12. <Insert manufacturer.>

2.2 EQUIPMENT

A. Coordinate Equipment Features:  Match components and interconnections for optimum performance of specified functions.

B. Equipment:  Modular type, using solid-state components, fully rated for continuous duty, unless otherwise indicated.  Select equipment for normal operation on input power usually supplied at 110 to 130 V, 60 Hz.

2.3 PREAMPLIFIERS

A. Comply with EIA SE-101-A; either separately mounted or as an integral part of power amplifier.

B. Output Power:  Plus 4 dB above 1 mW at matched power-amplifier load.

C. Total Harmonic Distortion:  Less than 1 percent.

D. Frequency Response:  Within plus or minus 2 dB from 20 to 20,000 Hz.

E. Input Jacks:  Minimum of two.  One matched for low-impedance microphone; the other matchable to cassette deck, CD player, or radio tuner signals without external adapters.

F. Minimum Noise Level:  Minus 55 dB below rated output.

G. Controls:  On/off, input levels, and master gain.

2.4 POWER AMPLIFIERS

A. Comply with EIA SE-101-A.

Edit first paragraph below to suit Project.

B. Output Power: [25] [70]  V, balanced line.

C. Frequency Response:  Within plus or minus 2 dB from 50 to 12,000 Hz.

D. Minimum Signal-to-Noise Ratio:  60 dB, at rated output.

E. Total Harmonic Distortion:  Less than 3 percent at rated power output from 50 to 12,000 Hz.

F. Output Regulation:  Less than 2 dB from full to no load.

G. Controls:  On/off, input levels, and low-cut filter.

H. Input Sensitivity:  Matched to preamplifier and providing full-rated output with a sound-pressure level of less than 10 dynes/sq. cm impinging on a speaker microphone or handset transmitter.

2.5 COMPONENTS

A. Microphone:  Comply with EIA SE-105.

1. Type:  Dynamic, with cardioid polar or omnidirectional characteristic.

2. Impedance:  150 ohms.

3. Frequency Response:  Uniform, 60 to 12,000 Hz.

4. Output Level:  Minus 58 dB minimum.

5. Finish:  Satin chrome.

6. Mounting:  Desk stand with weighted base and integral locking, press-to-talk switch.

Since microphones are portable items that can be plugged into any microphone outlet, retain first subparagraph below to specify quantities.  See Evaluations.

7. Quantity of Microphones:  Four, including one spare.

8. Quantity of Desk Stands:  Three.

Delete first paragraph and subparagraphs below if not required.  Paging access from intercommunication equipment may be similarly specified.

B. Telephone Paging Adapter:  Arranged to accept voice signals from telephone extension dialing access and to automatically provide amplifier input and program override for preselected zones.

1. Minimum Frequency Response:  Flat, 200 to 2500 Hz.

2. Impedance Matching:  Adapter matches telephone line to public address equipment input.

C. Equipment Cabinet:  Comply with EIA-310-D.  House amplifiers and auxiliary equipment.

1. Cabinet Housing:  Construct of 0.0478-inch (1.2-mm) steel, minimum, with front locking doors and standard EIA 19-inch (483-mm) racks.  Arrange for floor or wall mounting as indicated.  Size to house all equipment indicated plus spare capacity.  Include 20 percent minimum spare capacity for future equipment over and above space required for future cassette deck and CD player.

2. Power Provisions:  Install a single switch in cabinet to supply cabinet power distribution and electrical outlets, uniformly spaced, to accommodate ac-power cords of each item of equipment.

3. Ventilation:  A low-noise fan for forced-air cabinet ventilation.  Equip fan with a filtered input vent and connect to operate from 105- to 130-V ac, 60 Hz; separately fused and switchable and arranged to be powered when main cabinet power switch is on.

Coordinate paragraph and subparagraphs below with Drawings.

D. Cone-Type Loudspeakers:  Comply with EIA SE-103.

1. Minimum Axial Sensitivity:  EIA pressure rating of 45 dB.

2. Frequency Response:  Within plus or minus 3 dB from 50 to 15,000 Hz.

3. Size:  8 inches (200 mm) with 1-inch (25-mm) voice coil and minimum 5-oz. (140-g) ceramic magnet.

4. Minimum Dispersion Angle:  100 deg rees.

5. Rated Output Level:  10 W.

6. Matching Transformer:  Comply with EIA-160.  Full-power rated with four EIA standard taps.  Maximum insertion loss of 0.5 dB.

Coordinate subparagraph below with Drawings.

7. Surface-Mounting Units:  Ceiling, wall, or pendant mounting, as indicated, in steel back boxes, acoustically dampened.  Front face of at least 0.0478-inch (1.2-mm) steel and whole assembly rust proofed and shop primed for field painting.

Modify finish description below as required to suit aesthetic requirements.

8. Flush-Ceiling Mounting Units:  In steel back boxes, acoustically dampened.  Metal ceiling grille with baked, white-enamel finish.

Device below is specified as a sample.  Revise as required to suit Project and manufacturer's standard equipment.  Coordinate with Drawings.

E. Horn-Type Loudspeakers:  Comply with EIA SE-103.

1. Type:  Single-horn units, double-reentrant design, with minimum full-range power rating of 15 W.

2. Matching Transformer:  Comply with EIA-160.  Full-power rated with four EIA standard taps.  Maximum insertion loss of 0.5 dB.

3. Frequency Response:  Within plus or minus 3 dB from 250 to 12,000 Hz.

4. Dispersion Angle:  130 by 110 deg rees.

5. Mounting:  Integral bracket.

Delete paragraph and subparagraphs below where volume attenuator stations are not used.

F. Volume Attenuator Stations:  Wall-plate-mounted autotransformer type with paging priority feature.

1. Wattage Rating:  10 W, unless otherwise indicated.

2. Attenuation per Step:  3 dB, with positive off position.

3. Insertion Loss:  0.4 dB maximum.

Delete feature below unless desired to override local volume settings during paging announcements.  If retained, edit first subparagraph below to suit Project.

4. Attenuation Bypass Relay:  Single pole, double throw.  Connected to operate and bypass attenuation when paging feature is used.  Relay returns to normal position at end of paging transmission.

5. Label:  "PA Volume."

Edit first two paragraphs below to suit Project.

G. Microphone Outlets:  Three-pole, polarized, locking-type, microphone receptacles in single-gang boxes.  Equip wall outlets with a brushed stainless-steel device plate.  Equip floor outlets with gray tapered rubber or plastic cable nozzles and fixed outlet covers.

Delete first paragraph below unless equipment operates during a power outage.

H. Headphone Outlets (for Hearing Impaired):  Microphone receptacles in single-gang boxes.  Equip wall outlets with a brushed stainless-steel device plate.  Equip floor outlets with gray tapered rubber or plastic cable nozzles and fixed outlet covers.

I. Cable and Conductors:  Jacketed, twisted-pair and twisted-multipair, untinned, solid-copper conductors.

1. Insulation for Wire in Conduit:  Thermoplastic, not less than 1/32 inch (0.8 mm) thick.

2. Microphone Cables:  Neoprene jacketed, not less than 2/64 inch (0.8 mm) thick over shield with filled interstices.  Shield No. 34 AWG tinned, soft-copper strands formed into a braid or approved equivalent foil.  Shielding coverage on conductors is not less than 60 percent.

3. Plenum Cable:  Listed and labeled for plenum installation.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Wiring Method:  Install wiring in raceway except within consoles, desks, and counters.  Conceal cable and raceway except in unfinished spaces.

Select paragraph above or below.  Coordinate with Drawings.

B. Wiring Method:  Install wiring in raceway except within consoles, cabinets, desks, and counters and except in accessible ceiling spaces, and in gypsum-board partitions where cable wiring method may be used.  Use cable listed for plenum installation in environmental air spaces, including plenum ceilings.  Conceal cable except in unfinished spaces.

Modify paragraphs below to suit Project.

C. Install exposed cables parallel and perpendicular to surfaces or exposed structural members, and follow surface contours.  Secure and support cables by straps, staples, or similar fittings designed and installed to avoid damage to cables.  Secure cable at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, or fittings.

D. Wiring Within Enclosures:  Bundle, lace, and train conductors to terminal points with no excess.  Use lacing bars in cabinets.

E. Control-Circuit Wiring:  Install number and size of conductors as recommended by system manufacturer for control functions indicated.

F. Separation of Wires:  Separate speaker-microphone, line-level, speaker-level, and power wiring runs.  Install in separate raceways or, where exposed or in same enclosure, separate conductors at least 12 inches (300 mm) for speaker microphones and adjacent parallel power and telephone wiring.  Separate other intercommunication equipment conductors as recommended by equipment manufacturer.

G. Match input and output impedances and signal levels at signal interfaces.  Provide matching networks where required.

H. Identification of Conductors and Cables:  Color-code conductors and apply wire and cable marking tape to designate wires and cables to identify media in coordination with wiring diagrams.

I. Wall-Mounting Outlets:  Flush mounted.

J. Floor-Mounting Outlets:  Conceal in floor and install cable nozzles through outlet covers.  Secure outlet covers in place.  Trim with carpet in carpeted areas.

K. Conductor Sizing:  Unless otherwise indicated, size speaker circuit conductors from racks to loudspeaker outlets not smaller than No. 18 AWG and conductors from microphone receptacles to amplifiers not smaller than No. 22 AWG.

L. Ground cable shields and equipment to minimize ground loops, common-mode returns, noise pickup, cross talk and other impairments of sound quality.

3.2 FIELD QUALITY CONTROL

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect field-assembled components and equipment installations, including connections, and assist with operational tests.  Report results in writing.

B. Operational Test:  Perform tests that include originating program and page material at microphone outlets, preamplifier program inputs, and other inputs.  Verify proper signal routing and volume levels and freedom from noise and distortion.

C. Inspection:  Verify that units and controls are properly connected and labeled and interconnecting wires and terminals are identified.

D. Retesting:  Correct deficiencies, revising tap settings of speaker-line matching transformers where necessary to optimize volume and uniformity of sound levels, and retest.

E. Report test results in writing.

3.3 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain public address and music equipment.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 16726

PUBLIC ADDRESS AND MUSIC EQUIPMENT
16726 - 1

