Copyright 1998 AIA
MASTERSPEC
3/98


Copyright 1998, The American Institute of Architects (AIA)

SECTION 16740 - COMMUNICATION AND DATA-PROCESSING EQUIPMENT

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes wire, cable, connecting devices, installation, and testing for wiring systems to be used as signal pathways for voice and high-speed data transmission.

1.3 DEFINITIONS

Retain acronyms and abbreviations that remain after this Section has been edited.

A. EMI:  Electromagnetic interference.

B. IDC:  Insulation displacement connector.

C. LAN:  Local area network.

D. PVC:  Polyvinyl chloride.

E. STP:  Shielded twisted pair.

F. UTP:  Unshielded twisted pair.

1.4 SUBMITTALS

A. Product Data:  Include data on features, ratings, and performance for each component specified.

B. Shop Drawings:  Include dimensioned plan and elevation views of components.  Show access and workspace requirements.

1. System labeling schedules, including electronic copy of labeling schedules, as specified in Part 3, in software and format selected by Owner.

Include sample below when workstation outlet faceplates have critical features needing hands-on appraisal.

C. Samples:  For workstation outlet connectors, jacks, jack assemblies, and faceplates for color selection and evaluation of technical features.

D. Product Certificates:  Signed by manufacturers of cables, connectors, and terminal equipment certifying that products furnished comply with requirements.

E. Qualification Data:  For firms and persons specified in "Quality Assurance" Article.  Provide evidence of applicable registration or certification.

F. Field Test Reports:  Indicate and interpret test results for compliance with performance requirements.

G. Maintenance Data:  For products to include in maintenance manuals specified in Division 1.

1.5 QUALITY ASSURANCE

Association in paragraph below is an industry trade association.  See Editing Instruction No. 2 in the Evaluations.

A. Installer Qualifications:  An experienced installer who is a registered communication distribution designer certified by the Building Industry Consulting Service International.

B. Comply with NFPA 70.

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.6 COORDINATION

Edit paragraph below to specify coordination with other parties involved in finalizing communication and data-processing equipment.  See Editing Instruction No. 3 in the Evaluations.

A. Coordinate Work of this Section with Owner's telephone switch, telephone instrument, workstation, and LAN equipment suppliers.  Coordinate service entrance arrangement with local exchange carrier.

1. Meet jointly with representatives of above organizations and Owner's representatives to exchange information and agree on details of equipment arrangements and installation interfaces.

2. Record agreements reached in meetings and distribute record to other participants.

3. Adjust arrangements and locations of distribution frames, patch panels, and cross connects in equipment rooms and wiring closets to accommodate and optimize arrangement and space requirements of telephone switch and LAN equipment.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraph below to suit Project.

1. Cable:  250 feet (76 m) of each size and type used for Project.  Furnish on reels.

2. Patch-Panel Units:  One of each type for every six installed, but not less than one.

3. Connecting Blocks:  One of each type for every 25 installed, but not less than one.

4. Outlet Assemblies:  One of each type for every 25 installed, but not less than one.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary Specification.  Refer to Division 1 Section "Materials and Equipment."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

See Editing Instruction No. 1 in the Evaluations for cautions about naming products and manufacturers.

1. Cable:

a. Belden Wire & Cable Company.

b. Berk-Tek, Inc.

c. BIW Cable Systems, Inc.

d. Brand-Rex Co.; Unit of BICC Cables Corp.

e. Champlain Cable Corp.

f. Essex Group, Inc.; Telecommunications Products Division.

g. General Cable.

h. HeLix/HiTemp Cables, Inc.

i. Lucent Technologies, Inc.; Network Systems.

j. MM Cables, Communications Products.

k. Mohawk/CDT.

l. Montrose Products Co.

m. Northern Telecom, Inc.

n. Optical Cable Corp.

o. Panduit Corp.

p. Prestolite Wire & Cable.

q. Siecor Corp.

r. Teledyne Thermatics, Inc.

2. Terminal and Connector Components and Distribution Racks:

a. AMP, Inc.

b. Hubbell Premise Wiring, Inc.

c. International Connector and Cable Corp.

d. Leviton Mfg. Co., Inc.; Telcom Division.

e. Lucent Technologies, Inc.; Network Systems.

f. Panduit Corporation.

g. Saunders Telcom.

h. Thomas & Betts, Electrical.

2.2 SYSTEM REQUIREMENTS

A. General:  Coordinate the features of materials and equipment so they form an integrated system.  Match components and interconnections for optimum future performance.

Modify percentage below to suit Project.

B. Expansion Capability:  Unless otherwise indicated, provide spare fibers and conductor pairs in cables, positions in patch panels, cross connects, and terminal strips, and space in backbone cable trays and wireways to accommodate 20 percent future increase in active workstations.

2.3 MOUNTING ELEMENTS

A. Cable Trays:  Comply with Division 16 Section "Cable Trays."

B. Raceways and Boxes:  Comply with Division 16 Section "Raceways and Boxes."

C. Backboards:  3/4-inch (19-mm) interior-grade, fire-resistive-treated plywood.

Delete paragraph below if all cross-connect and patch panels are mounted on backboards.  Coordinate with Drawings.

D. Distribution Racks:  Freestanding and wall-mounting, modular-steel units designed for telecommunications terminal support and coordinated with dimensions of units to be supported.

Revise dimensions in subparagraph below to suit Project, or delete subparagraph and indicate on Drawings.

1. Approximate Module Dimensions:  84 inches (2130 mm) high by 22 inches (560 mm) wide.

2. Finish:  Baked-polyester powder coat.

2.4 TWISTED-PAIR CABLES, CONNECTORS, AND TERMINAL EQUIPMENT

Revise category numbers below to coordinate with "Application of Media" Article in Part 3.

A. Listed as complying with Categories 3 or 5 of EIA/TIA-568-A.

B. Conductors:  Solid copper.

Select UTP or STP cable and connecting hardware in paragraphs below to suit Project.

C. UTP Cable:  Comply with EIA/TIA-568-A.  Four thermoplastic-insulated, individually twisted pairs of conductors; No. 24 AWG, color-coded; enclosed in PVC jacket.

D. STP Workstation Cable:  Comply with EIA/TIA-568-A.  Two thermoplastic-insulated, individually twisted pairs of conductors; No. 22 AWG, color-coded, overall aluminum and polyester shield and No. 22 AWG tinned-copper drain wire; enclosed in PVC jacket.

E. UTP and STP Plenum Cable:  Listed for use in air-handling spaces.  Features are as specified above, except materials are modified as required for listing.

Several types of IDCs below are in common use.  See Editing Instruction No. 4 in the Evaluations.  Coordinate with Drawings.

F. UTP Cable Connecting Hardware:  Comply with EIA/TIA-568-A.  IDC type, using modules designed for punch-down caps or tools.

1. IDC Terminal Block Modules:  Integral with connector bodies, including plugs and jacks where indicated.

2. IDC Connecting Hardware:  Consistent throughout Project.

G. STP Cable Connecting Hardware:  Comply with EIA/TIA-568-A for connectors, plugs, and jack assemblies.

Delete paragraph below if cross connection is accomplished exclusively on patch panels.  Coordinate with Drawings.

H. Cross-Connect Panel:  Modular array of IDC terminal blocks arranged to terminate building cables and permit interconnection between cables.

Revise quantity in subparagraph below to suit Project.

1. Number of Terminals per Field:  One for each conductor in assigned cables.

2. Mounting:  Backboard or rack as indicated.

I. Patch Panel:  Modular panels housing multiple, numbered jack units with IDC-type connectors at each jack for permanent termination of pair groups of installed cables.

Select number of jacks per field from options in subparagraph below.  Coordinate with Drawings for quantity of fields.

1. Number of Jacks per Field:  [One for each four-pair UTP cable or two-pair STP cable indicated] [One for each four-pair conductor group of indicated cables, plus spares and blank positions adequate to satisfy specified expansion criteria].

Coordinate subparagraph below with Drawings.

2. Mounting:  [Backboard] [Rack].

Revise first two paragraphs below if other than RJ-45 modular connectors are required for some applications.  See Editing Instruction No. 6 in the Evaluations.

J. Jacks and Jack Assemblies for UTP Cable:  Modular, color-coded, RJ-45 receptacle units with integral IDC-type terminals.  Use keyed jacks for data service.

K. UTP Patch Cords:  Four-pair cables in 48-inch (1200-mm) lengths, terminated with RJ-45 plug at each end.  Use keyed plugs for data service.

L. STP Patch Cords:  Two-pair cables in 48-inch (1200-mm) lengths, terminated with STP plug connectors at both ends.  Match plug connectors with patch-panel connectors.

Edit paragraph and subparagraphs below to suit Project.  Coordinate with other items specified to be mounted in workstation faceplates.  Coordinate with Drawings.

M. Workstation Outlets:  Dual jack-connector assemblies mounted in single or multigang faceplate.

1. Faceplate:  High-impact plastic; color as selected by Architect.

2. Mounting:  Flush, unless otherwise indicated.

3. Legend:  Factory label top jack, "Voice" and bottom jack, "Data"; by silk-screening or engraving.

2.5 FIBER-OPTIC CABLES, CONNECTORS, AND TERMINAL EQUIPMENT

A. Cables:  Factory fabricated, jacketed, low loss, glass type, fiber optic, multimode, graded index, operating at 850 and 1300 nm.

1. Workstation, Strands per Cable:  Two.

2. Backbone, Strands per Cable:  12, unless otherwise indicated.

3. Dimensions:  62.5-micrometer core diameter, 125-micrometer cladding diameter.

4. Maximum Attenuation:  Minus 3.75 dB/km at 850 nm; minus 1.5 dB/km at 1300 nm.

5. Minimum Modal Bandwidth:  160 MHz/km at 850 nm; 500 MHz/km at 1300 nm.

6. Operating Temperature Range:  Minus 20 to plus 70 deg C.

B. Plenum Cable:  Listed for use in plenums.

C. Cable Connectors:  Quick-connect, simplex- and duplex-type SC couplers with self-centering, axial alignment mechanisms.  Insertion loss not more than 0.7 dB.

D. Patch Panel:  Modular panels housing multiple-numbered duplex cable connectors.

1. Permanent Connection:  Permanently connect one end of each connector module to installed cable fiber.

Coordinate subparagraph below with Drawings.

2. Number of Connectors per Field:  One for each fiber of cable or cables assigned to field, plus spares and blank positions adequate to satisfy specified expansion criteria.

Coordinate subparagraph below with Drawings.

3. Mounting:  [Backboard] [Rack].

E. Patch Cords:  Dual fiber cables in 36-inch (900-mm) lengths.

1. Terminations:  Two duplex connectors arranged to mate with patch-panel connectors, one at each end of each fiber in cord.

Delete paragraph and subparagraphs below or edit to suit Project.  Coordinate with other items specified to be mounted in workstation faceplates.  Edit to be compatible with plug-and-jack type specified for telephone service.  Coordinate with Drawings.  See Editing Instruction No. 6 in the Evaluations.

F. Workstation Outlets:  Flush dual fiber-optic connector assemblies mounted in two-gang faceplate with flush dual RJ-45 jack assembly.

1. Faceplate:  High-impact plastic; color as selected by Architect.

2. Mounting:  Flush, unless otherwise indicated.

3. Legend:  Factory label fiber-optic connectors, "Data" and RJ-45 jacks, "Voice."

2.6 IDENTIFICATION PRODUCTS

Select appropriate Section in paragraph below.

A. Comply with Division 16 Section ["Basic Electrical Materials and Methods"] ["Electrical Identification"] and the following:

Retain below with either paragraph above.

1. Cable Labels:  Self-adhesive vinyl or vinyl-cloth wraparound tape markers, machine printed with alphanumeric cable designations.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine pathway elements intended for cable.  Check raceways, cable trays, and other elements for compliance with space allocations, installation tolerances, hazards to cable installation, and other conditions affecting installation.  Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 APPLICATION OF MEDIA

Edit this Article to suit Project.  Select media types used for Project applications.

A. Backbone Cable for Data Service:  Use UTP cable complying with Category 5 of EIA/TIA-568-A, fiber-optic cable for runs between equipment rooms and wiring closets and for runs between wiring closets.

Select voice backbone media from options in paragraph below.

B. Backbone Cables for Voice Service:  Use UTP cable complying with Category  [3] [5] of EIA/TIA-568-A for runs between equipment rooms and wiring closets and for runs between wiring closets.

Select horizontal data media from options in paragraph below.

C. Horizontal Cables for Data Service:  Use [UTP cable complying with Category 5 of EIA/TIA-568-A] [STP cable complying with Category 5 of EIA/TIA-568-A, fiber-optic cable] for runs between wiring closets and workstation outlets.

Select horizontal voice media from options below.

D. Horizontal Cables for Voice Service:  Use UTP cable complying with Category  [3] [5] of EIA/TIA-568-A for runs between wiring closets and workstation outlets.

3.3 INSTALLATION

Select and edit one of first two paragraphs below to suit Project.

A. Wiring Method:  Install wiring in raceway and cable tray except within consoles, cabinets, desks, and counters.  Conceal raceway and wiring except in unfinished spaces.

B. Wiring Method:  Install wiring in raceway and cable tray except within consoles, cabinets, desks, and counters and except in accessible ceiling spaces and in gypsum board partitions where cable wiring method may be used.  Use UL-listed plenum cable in environmental air spaces, including plenum ceilings.  Conceal raceway and wiring except in unfinished spaces.

Retain category below to match selection in Part 2.

C. Install cable using techniques, practices, and methods that are consistent with Category  [3] [5] rating of components and that ensure Category  [3] [5] performance of completed and linked signal paths, end to end.

D. Install cable without damaging conductors, shield, or jacket.

E. Do not bend cable in handling or in installing to smaller radii than minimums recommended by manufacturer.

F. Pull cables without exceeding cable manufacturer's recommended pulling tensions.

1. Pull cables simultaneously if more than one is being installed in the same raceway.

2. Use pulling compound or lubricant if necessary.  Use compounds that will not damage conductor or insulation.

3. Use pulling means, including fish tape, cable, rope, and basket-weave wire/cable grips, that will not damage media or raceway.

G. Install exposed cable parallel and perpendicular to surfaces or exposed structural members, and follow surface contours where possible.

H. Secure and support cable at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

I. Wiring within Wiring Closets and Enclosures:  Provide adequate length of conductors.  Train conductors to terminal points with no excess.  Use lacing bars to restrain cables, to prevent straining connections, and to prevent bending cables to smaller radii than minimums recommended by manufacturer.

J. Separation of Wires:  Comply with EIA/TIA-569 rules for separating unshielded copper communication and data-processing equipment cables from potential EMI sources, including electrical power lines and equipment.

K. Make splices, taps, and terminations only at indicated outlets, terminals, and cross-connect and patch panels.

L. Use splice and tap connectors compatible with media types.

3.4 GROUNDING

Revise this Article to suit Project.  Coordinate with Drawings.

A. Comply with Division 16 Section "Grounding."

B. Ground cable shields, drain conductors, and equipment to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.

For considerations about bonding shields to ground in paragraph below, see Editing Instruction No. 5 in the Evaluations.

C. Bond shields and drain conductors to ground at only one point in each circuit.

D. Signal Ground Terminal:  Locate in each equipment room and wiring closet.  Isolate from power system and equipment grounding.

E. Signal Ground Bus:  Mount on wall of main equipment room with standoff insulators.

F. Signal Ground Backbone Cable:  Extend from signal ground bus to signal ground terminal in each wiring closet and equipment room.

3.5 INSTALLATION IN EQUIPMENT ROOMS AND WIRING CLOSETS

Coordinate paragraphs below with Drawings.

A. Line walls with plywood backboards, floor to ceiling.

B. Mount patch panels, terminal strips, and other connecting hardware on backboards, unless otherwise indicated.

C. Group connecting hardware for cables into separate logical fields.

D. Use patch panels to terminate cables entering the space, unless otherwise indicated.

3.6 IDENTIFICATION

Select appropriate Section in paragraph below.

A. Identify system components complying with applicable requirements in Division 16 Section ["Basic Electrical Materials and Methods"] ["Electrical Identification"] and the following Specifications.

B. System:  Use a unique, three-syllable alphanumeric designation for each cable, and label cable and jacks, connectors, and terminals to which it connects with the same designation.  Use logical and systematic designations for facility's architectural arrangement.

1. First syllable identifies and locates wiring closet or equipment room where cable originates.

2. Second syllable identifies and locates cross-connect or patch-panel field in which cable terminates.

3. Third syllable designates type of media (copper or fiber) and position occupied by cable pairs or fibers in the field.

C. Workstation:  Label cables within outlet boxes.

D. Distribution Racks and Frames:  Label each unit and field within that unit.

E. Within Connector Fields, in Wiring Closets and Equipment Rooms:  Label each connector and each discrete unit of cable-terminating and connecting hardware.  Where similar jacks and plugs are used for both communication and data-processing equipment, use a different color for jacks and plugs of each service.

F. Cables, General:  Label each cable within 4 inches (100 mm) of each termination and tap, where it is accessible in a cabinet or junction or outlet box, and elsewhere as indicated.

G. Exposed Cables and Cables in Cable Trays and Wire Troughs:  Label each cable at intervals not exceeding 15 feet (4.5 m).

H. Cable Schedule:  Post in prominent location in each wiring closet and equipment room.  List incoming and outgoing cables and their designations, origins, and destinations.  Protect with rigid frame and clear plastic cover.  Provide electronic copy of final comprehensive schedules for Project, in software and format selected by Owner.

3.7 FIELD QUALITY CONTROL

A. Testing Agency:  Owner will engage a qualified testing agency to perform field quality-control testing.

Delete paragraph above or below.  Delete above if Contractor is responsible for field quality-control testing.  Retain below if testing-firm services are included in Contract Sum.

B. Testing:  On installation of cable and connectors, demonstrate product capability and compliance with requirements.  Test each signal path for end-to-end performance from each end of all pairs installed.  Remove temporary connections when tests have been satisfactorily completed.

Retain two subparagraphs below with either paragraph above.

1. Copper Cable Procedures:  Inspect for physical damage and test each conductor signal path for continuity and shorts.  Use Class 2 bidirectional Category 5 tester.  Test for faulty connectors, splices, and terminations.  Test according to EIA/TIA-TSB 67, "Transmission Performance Specifications for Field Testing of Unshielded Twisted-Pair Cabling Systems." Link performance for UTP cables must meet minimum criteria of EIA/TIA-568-A.

Referenced tests in NETA ATS include inspection procedures to verify physical condition, and tests and measurements to verify proper installation.

2. Fiber-Optic Cable Procedures:  Perform each visual and mechanical inspection and electrical test, including optional procedures, stated in NETA ATS, Section 7.25.  Certify compliance with test parameters and manufacturer's written recommendations.  Test optical performance with optical power meter capable of generating light at all appropriate wavelengths.

C. Correct malfunctioning units at Project site, where possible, and retest to demonstrate compliance; otherwise, remove and replace with new units and retest.

3.8 CLEANING

A. After completing system installation, including outlet fittings and devices, inspect exposed finish.  Remove burrs, dirt, and construction debris and repair damaged finish, including chips, scratches, and abrasions.

3.9 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain systems.

1. Train Owner's maintenance personnel on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining equipment and schedules.

2. Train designated personnel in cable-plant management operations, including changing signal pathways for different workstations, rerouting signals in failed cables, and extending wiring to establish new workstation outlets.

3. Review data in maintenance manuals.  Refer to Division 1 Section "Contract Closeout."

Delete subparagraph above or below depending on which Section is retained in Division 1.

4. Review data in maintenance manuals.  Refer to Division 1 Section "Operation and Maintenance Data."

5. Schedule training with Owner, through Architect, with at least seven days' advance notice.

END OF SECTION 16740

COMMUNICATION AND DATA-PROCESSING EQUIPMENT
16740 - 1

