Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99


MASTERSPEC Short Form Copyright 1999, The American Institute of Architects (AIA)

SECTION 16740 - COMMUNICATIONS AND DATA-PROCESSING EQUIPMENT

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes copper wire and cable and connecting devices and their installation as signal pathways for voice and high-speed data transmission in buildings.

1.2 SUBMITTALS

A. Product Data:  Include data on features, ratings, and performance for each communication and data-processing component indicated.

B. Shop Drawings:  Include dimensioned plan and elevation views of components.  Show access and workspace requirements.

1. System labeling schedules, including electronic copy of labeling schedules, as specified in Part 3, in software and format selected by Owner.

2. Wiring Diagrams:  Power, signal, and control wiring.

C. Field quality-control test reports.

D. Operation and maintenance data.

1.3 QUALITY ASSURANCE

Association in first paragraph below is an industry trade association.  See Editing Instruction No. 2 in the Evaluations.

A. Installer Qualifications:  An experienced installer who is a registered communication distribution designer certified by the Building Industry Consulting Service International.

B. Comply with NFPA 70.

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.4 COORDINATION

Edit paragraph below to specify coordination with other parties involved in finalizing communication and data-processing connections.  See Editing Instruction No. 3 in the Evaluations.

A. Coordinate Work of this Section with Owner's telephone switch, telephone instrument, workstation, and LAN equipment suppliers.  Coordinate service entrance arrangement with local exchange carrier.

1. Meet jointly with representatives of above organizations and Owner's representatives to exchange information and agree on details of equipment arrangements and installation interfaces.

2. Record agreements reached in meetings and distribute record to other participants.

3. Adjust arrangements and locations of cross-connect panels and patch panels in equipment rooms and wiring closets to accommodate and optimize arrangement and space requirements of telephone switch and LAN equipment.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Cable:

a. Belden Wire & Cable Company.

b. Berk-Tek, Inc.

c. BIW Cable Systems, Inc.

d. Brand-Rex Co.; Unit of BICC Cables Corp.

e. Champlain Cable Corp.

f. Essex Group, Inc.; Telecommunications Products Division.

g. General Cable.

h. HeLix/HiTemp Cables, Inc.

i. Lucent Technologies, Inc.; Network Systems.

j. MM Cables, Communications Products.

k. Mohawk/CDT.

l. Montrose Products Co.

m. Northern Telecom, Inc.

n. Panduit Corp.

o. Prestolite Wire & Cable.

p. Siecor Corp.

q. Teledyne Thermatics, Inc.

r. <Insert manufacturer.>

2. Terminal and Connector Components and Distribution Racks:

a. AMP, Inc.

b. Hubbell Premise Wiring, Inc.

c. International Connector and Cable Corp.

d. Leviton Mfg. Co., Inc.; Telcom Division.

e. Lucent Technologies, Inc.; Network Systems.

f. Panduit Corporation.

g. Saunders Telcom.

h. Thomas & Betts, Electrical.

i. <Insert manufacturer.>

2.2 SYSTEM REQUIREMENTS

A. General:  Coordinate the features of materials and equipment so they form an integrated system.  Match components and interconnections for optimum future performance.

Modify percentage below to suit Project.

B. Expansion Capability:  Unless otherwise indicated, provide spare conductor pairs in cables, and positions in patch panels and cross connect panels and space in backbone cable trays and wireways to accommodate 20 percent future increase in active workstations.

2.3 MOUNTING ELEMENTS

A. Cable Trays:  Comply with Division 16 Section "Cable Trays."

B. Raceways and Boxes:  Comply with Division 16 Section "Raceways and Boxes."

C. Backboards:  3/4-inch (19-mm) interior-grade, fire-resistive-treated plywood.

2.4 TWISTED-PAIR CABLES, CONNECTORS, AND TERMINAL EQUIPMENT

Revise category numbers in first paragraph below to coordinate with "Application of Media" Article in Part 3.

A. Listed as complying with Categories 3 or 5 of EIA/TIA-568-A.

B. Conductors:  Solid copper.

Select UTP or STP cable and connecting hardware in paragraphs below to suit Project.

C. UTP Cable:  Comply with EIA/TIA-568-A.  Four thermoplastic-insulated, individually twisted pairs of conductors; No. 24 AWG, color-coded; enclosed in PVC jacket.

D. STP Workstation Cable:  Comply with EIA/TIA-568-A.  Two thermoplastic-insulated, individually twisted pairs of conductors; No. 22 AWG, color-coded, overall aluminum and polyester shield and No. 22 AWG tinned-copper drain wire; enclosed in PVC jacket.

E. UTP and STP Plenum Cable:  Listed for use in air-handling spaces.  Features are as specified above, except materials are modified as required for listing.

Several types of IDCs below are in common use.  See Editing Instruction No. 4 in the Evaluations.  Coordinate with Drawings.

F. UTP Cable Connecting Hardware:  Comply with EIA/TIA-568-A.  IDC type, using modules designed for punch-down caps or tools.

1. IDC Terminal Block Modules:  Integral with connector bodies, including plugs and jacks where indicated.

2. IDC Connecting Hardware:  Consistent throughout Project.

G. STP Cable Connecting Hardware:  Comply with EIA/TIA-568-A for connectors, plugs, and jack assemblies.

Delete first paragraph below if cross connection is accomplished exclusively on patch panels.  Coordinate with Drawings.

H. Cross-Connect Panel:  Modular array of IDC terminal blocks arranged to terminate building cables and permit interconnection between cables.

Revise quantity in subparagraph below to suit Project.

1. Number of Terminals per Field:  One for each conductor in assigned cables.

2. Mounting:  Backboard.

I. Patch Panel:  Modular panels housing multiple, numbered jack units with IDC-type connectors at each jack for permanent termination of pair groups of installed cables.

Select number of jacks per field from options in subparagraph below.  Coordinate with Drawings for quantity of fields.

1. Number of Jacks per Field:  One for each four-pair [UTP cable or two-pair STP cable indicated] [conductor group of indicated cables, plus spares and blank positions adequate to satisfy specified expansion criteria].

Coordinate subparagraph below with Drawings.

2. Mounting:  Backboard.

Revise first two paragraphs below if other than RJ-45 modular connectors are required for some applications.  See Editing Instruction No. 6 in the Evaluations.

J. Jacks and Jack Assemblies for UTP Cable:  Modular, color-coded, RJ-45 receptacle units with integral IDC-type terminals.  Use keyed jacks for data service.

K. UTP Patch Cords:  Four-pair cables in 48-inch (1200-mm) lengths, terminated with RJ-45 plug at each end.  Use keyed plugs for data service.

L. STP Patch Cords:  Two-pair cables in 48-inch (1200-mm) lengths, terminated with STP plug connectors at both ends.  Match plug connectors with patch-panel connectors.

Edit below to suit Project.  Coordinate with other items specified to be mounted in workstation faceplates.  Coordinate with Drawings.

M. Workstation Outlets:  Dual jack-connector assemblies mounted in single or multigang faceplate.

1. Faceplate:  High-impact plastic; color as selected by Architect.

2. Mounting:  Flush, unless otherwise indicated.

3. Legend:  Factory label top jack, "Voice" and bottom jack, "Data"; by silk-screening or engraving.

2.5 IDENTIFICATION PRODUCTS

Select appropriate Section in paragraph below.

A. Comply with Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]" and the following:

Retain below with paragraph above.

1. Cable Labels:  Self-adhesive vinyl or vinyl-cloth wraparound tape markers, machine printed with alphanumeric cable designations.

PART 3 -  EXECUTION

3.1 APPLICATION OF MEDIA

Edit this Article to suit Project.  Select media types used for Project applications.

A. Backbone Cable for Data Service:  Use UTP cable complying with Category 5 of EIA/TIA-568-A for runs between equipment rooms and wiring closets and for runs between wiring closets.

Select voice backbone media category from options in paragraph below.

B. Backbone Cables for Voice Service:  Use UTP cable complying with Category  [3] [5] of EIA/TIA-568-A for runs between equipment rooms and wiring closets and for runs between wiring closets.

Select horizontal data media from options in paragraph below.

C. Horizontal Cables for Data Service:  Use [UTP cable complying with Category 5 of EIA/TIA-568-A] [STP cable complying with Category 5 of EIA/TIA-568-A] for runs between wiring closets and workstation outlets.

Select horizontal voice media from options below.

D. Horizontal Cables for Voice Service:  Use UTP cable complying with Category  [3] [5] of EIA/TIA-568-A for runs between wiring closets and workstation outlets.

3.2 INSTALLATION

Edit below to define wiring method for communication and data-processing equipment for Project.

A. Wiring Method:  Install wiring in raceway and cable tray except within consoles, cabinets, desks, and counters and except in unfinished spaces, accessible ceiling spaces, and within gypsum board partitions, where cable wiring method may be used unless otherwise indicated.  Use cable listed for plenum use in environmental air spaces, including plenum ceilings.  Conceal raceway and wiring except in unfinished spaces.

B. Install cable and connectors using techniques, practices, and methods that are consistent with specified category ratings of components and that ensure performance of completed and linked signal paths, end to end, that comply with those ratings.

C. Install cable without damaging conductors, shield, or jacket.

D. Install exposed cable parallel and perpendicular to surfaces or exposed structural members, and follow surface contours where possible.

E. Secure and support cable at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

F. Wiring within Wiring Closets and Enclosures:  Use exposed cables and provide adequate length of conductors.  Train conductors to terminal points with no excess.  Use lacing bars to restrain cables, to prevent straining connections, and to prevent bending cables to smaller radii than minimums recommended by manufacturer.

G. Separation of Wires:  Comply with EIA/TIA-569 rules for separating unshielded copper communication and data-processing equipment cables from potential EMI sources, including electrical power lines and equipment.

H. Make splices, taps, and terminations only at indicated outlets, terminals, and cross-connect and patch panels.

I. Use splice and tap connectors compatible with media types and category ratings.

3.3 GROUNDING

Revise this Article to suit Project.  Coordinate with Drawings.

A. Comply with Division 16 Section "Grounding and Bonding."

B. Ground cable shields, drain conductors, and equipment to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other signal quality impairments.

For considerations about bonding shields to ground in first paragraph below, see Editing Instruction No. 5 in the Evaluations.

C. Bond shields and drain conductors to ground at only one point in each circuit.

D. Signal Ground Terminal:  Locate in each equipment room and wiring closet.  Isolate from power system and equipment grounding except for minimum cross-connection required by NFPA 70.

E. Signal Ground Bus:  Mount on wall of main equipment room with standoff insulators.

F. Signal Ground Backbone Cable:  Extend from signal ground bus to signal ground terminal in each wiring closet and equipment room.

3.4 INSTALLATION IN EQUIPMENT ROOMS AND WIRING CLOSETS

Coordinate this Article with Drawings.

A. Line walls with plywood backboards, floor to ceiling.

B. Mount cross-connect panels, patch panels, and other connecting hardware on backboards, unless otherwise indicated.

C. Group connecting hardware for cables into separate logical fields.

D. Use patch panels to terminate cables entering the space, unless otherwise indicated.

3.5 IDENTIFICATION

A. Identify system components complying with applicable requirements in Division 16 Section "[Basic Electrical Materials and Methods] [Electrical Identification]" and the following Specifications.

B. System:  Use a unique, three-syllable alphanumeric designation for each cable, and label cable and jacks, connectors, and terminals to which it connects with the same designation.  Use logical and systematic designations for facility's architectural arrangement.

1. First syllable identifies and locates wiring closet or equipment room where cable originates.

2. Second syllable identifies and locates cross-connect or patch-panel field in which cable terminates.

3. Third syllable designates type of media (copper or fiber) and position occupied by cable pairs or fibers in the field.

C. Workstation:  Label cables within outlet boxes.

D. Label each unit uniquely, and label each field in each unit.

E. Within Connector Fields, in Wiring Closets and Equipment Rooms:  Label each connector and each discrete unit of cable-terminating and connecting hardware.  Where similar jacks and plugs are used for both voice communication and data-processing, use a different color for jacks and plugs of each service.

F. Cables, General:  Label each cable within 4 inches (100 mm) of each termination and tap, and where it is accessible in a cabinet or junction or outlet box, and elsewhere as indicated.

G. Exposed Cables and Cables in Cable Trays and Wire Troughs:  Label each cable at intervals not exceeding 15 feet (4.5 m).

H. Cable Schedule:  Post in prominent location in each wiring closet and equipment room.  List incoming and outgoing cables and their designations, origins, and destinations.  Protect with rigid frame and clear plastic cover.  Provide electronic copy of final comprehensive schedules for Project, in software and format selected by Owner.

3.6 FIELD QUALITY CONTROL

A. Testing:  After installation of cable and connectors, demonstrate product capability and compliance with requirements.  Test each signal path for end-to-end performance from each end of all pairs installed.  Use temporary connections at [cross connections] [and] [patch panels] so connectors are tested along with connectors.  Remove temporary connections when tests have been satisfactorily completed.

1. Procedures:  Test each conductor signal path for continuity and shorts and inspect for physical damage.  Use Class 2 bidirectional Category 5 tester.  Test for faulty connectors, splices, and terminations.  Test UTP cables according to EIA/TIA-TSB 67, "Transmission Performance Specifications for Field Testing of Unshielded Twisted-Pair Cabling Systems."  Link performance for UTP cables must meet minimum criteria of EIA/TIA-568-A.

2. Make similar tests of STP cables.

B. Correct malfunctioning units at Project site, where possible, and retest to demonstrate compliance;  otherwise, remove and replace with new units and retest.

C. Report test results in writing.

3.7 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain communications and data-processing equipment.  Refer to Division 1 Section "[Closeout Procedures] [Demonstration and Training]."

END OF SECTION 16740

COMMUNICATIONS AND DATA-PROCESSING EQUIPMENT
16740 - 1

