SIEMENS LCP3000EZ

SECTION 16146
PROGRAMMABLE LOW VOLTAGE LIGHTING CONTROL SYSTEM
PART 1 -  GENERAL

1.01 RELATED DOCUMENTS

A. The work covered in this section is subject to all of the requirements in the General Conditions of the specifications that apply.

B. Contractor shall coordinate all of the work in this section with all the trades covered in the other sections of the specification to provide a complete and operative system.

C. [Related Sections include the following:

1. Section 16442 – Panelboards

2. Section 16475 – Circuit Breakers and Fusible Switches – Low Voltage

3. Section 16911 – Power Management System

4. Section 15xxx – Building Automation /Energy Management Systems  ]
1.02 SUMMARY

A. Extent of lighting control system work is indicated by drawings and by the requirements of this section.  It is defined to include low voltage lighting control panels, switch inputs and wiring. 

B. Type of lighting control equipment and wiring specified in this section include the following:

1. Low Voltage Lighting Control Panels

2. Requirements are indicated elsewhere in these specifications for work including, but not limited to, raceways and electrical boxes and fittings required for installation of control equipment and wiring.

1.03 SUBMITTALS

A. Submittal documentation shall be furnished by the manufacturer for approval by the Engineer and must be approved in writing prior to shipment of any equipment from the manufacturer.  It shall consist of:

1. Bill of Materials - Manufacturer shall submit in bill of material form an itemized list of all materials being supplied to meet the specifications.

2. Product Data - Manufacturer shall submit data on each of the components proposed for the low voltage lighting control system.

3. One-Line Diagram - Manufacture shall submit a one-line diagram of the proposed system configuration with relative placement of all equipment.

4. Typical Wiring Diagrams - Submit typical wiring diagrams for all proposed equipment with sufficient details for all interconnections.

B. Programming - The manufacture shall provide initial programming of the system.  Contractor shall identify relays and circuits.

C. Commissioning - After the system has been installed, the network wiring and telephone lines are operational; the contractor shall secure the services of a factory-trained representative of the manufacturer to verify correct operation of all system components.  The factory-trained representatives shall verify that the contractor has properly installed and interconnected all supplied components.  They shall start up all equipment and demonstrate that it meets the requirements of this specification.

D. Training - As part of the commissioning procedures, the manufacturer shall provide a minimum of 8 hours training for the owner=s representative in the operation of the system.

E. Technical Support - The manufacturer shall provide free telephone support to the owner for the duration of the warranty period.

F. Extended Service Coverage - Maintenance agreements shall be available from the manufacturer to provide service for the system both during and after the warranty period.
1.04 PRODUCT SUPPORT
A. Programming - The manufacture shall provide initial programming of the system.  Contractor shall identify relays and circuits.

B. Commissioning - After the system has been installed, the network wiring and telephone lines are operational; the contractor shall secure the services of a factory-trained representative of the manufacturer to verify correct operation of all system components.  The factory-trained representatives shall verify that the contractor has properly installed and interconnected all supplied components.  They shall start up all equipment and demonstrate that it meets the requirements of this specification.

C. Training - As part of the commissioning procedures, the manufacturer shall provide a minimum of 8 hours training for the owner=s representative in the operation of the system.

D. Technical Support - The manufacturer shall provide free telephone support to the owner for the duration of the warranty period.

E. Extended Service Coverage - Maintenance agreements shall be available from the manufacturer to provide service for the system both during and after the warranty period.

1.05 QUALITY ASSURANCE 

A. UL & cUL APPROVALS 

1. The control panels shall be tested and listed under the UL 916 Energy Management Equipment standards and CSA C22.2 #205.

B. NEC COMPLIANCE
1. The control system shall comply with all applicable National Electrical Codes regarding electrical wiring standards.

C. NEMA COMPLIANCE
1. The control system shall comply with all applicable portions of the NEMA standards regarding the types of electrical equipment enclosures.

D. COMPONENT PRE-TESTING
1. All control equipment shall undergo strict inspection standards.
E. SYSTEM CHECKOUT
F. INITIAL PROGRAMMING

1. The lighting control equipment manufacturer shall provide initial set-up and programming of the software program controlling the lighting relays.  Relay panel schedules and low-voltage relay documentation shall be the responsibility of the Contractor to collect and furnish to the equipment manufacturer for initial program setup.

G. [MANUFACTURER
1. Manufacturer shall have a minimum of ten years experience in control systems.  Manufacturer shall provide off the shelf control products from its inventory.  Control systems that require custom assembly and sizing shall not be acceptable.   Manufacturer shall be:


a. SIEMENS Energy and Automation, Inc.

3333 Old Milton Parkway

Alpharetta, GA 30005  

1-800-964-4114 

Product shall be SIEMENS instabus Lighting Control panel or pre-approved equal.] 

PART 2 -  PRODUCTS

2.01 MATERIALS AND COMPONENTS

A. SYSTEM DESCRIPTION

1. The lighting control system shall consist of low voltage relay control panels that are able to network. Each panel is to be made of distributed logic components that are programmable, addressable and do not require a central operator for control. The system shall be modular in design and scaleable for future expansion of the system. 


2. Each low voltage lighting control panel shall contain microprocessor controlled input or control relay modules each containing an individual microprocessor. 

3. Programmable intelligence shall include Time-Of-Day control, 32 holiday dates, warn occupants of an impending off, timed outputs, preset control, auto daylight savings, control based on outdoor light level, optional astronomical clock w/offsets and local control.  

4. Each low voltage lighting control panel shall offer 8, 16, 24, or 32 programmable switch inputs and 8, 16, 24, 32, 40 or 48 programmable control relays.

5. The control system shall provide networking between sets of up to ten lighting control panels without adding communication or networking cards in each of these ten panels.  The control system network may support no less than 500 control panels.  Sets of up to ten lighting control panels shall be wired to the same line (twisted pair network). Networking between lines shall be possible via twisted pair with a Line Coupler. All inputs (no limitation) are transferable over the network to create any switching pattern required. 

6. A set of up to ten low voltage lighting control panels with up to 320 inputs and 480 relay outputs shall be able to network without using communication or networking cards in any of these ten panels. Each panel shall contain an RS232 interface module for access to and configuration of any of the ten control panels. The set of up to ten low voltage lighting control panels shall consist of a base panel and up to nine expansion panels. The base panel shall be marked as Panel A, the expansion panels shall be marked as Panel B, Panel C, Panel D, Panel E, Panel F, Panel G, Panel H, Panel J and Panel K.

7. Panel A (first panel) shall provide up to 32 programmable switch inputs, up to 48 programmable control relays, an RS232 interface module for access to and configuration of any of the set of ten control panels, a time-clock with four time channels shall be optional.
a. Additional options for Panel A
1) Time-clock with sixteen channels

2) Dual Sensor for outdoor ambient light level based control and temperature monitoring.
3) Touch Panel user control interface 
4) Key switch interface

5) Up to two motion sensors
6) IP Interface for Internet Protocol access via LAN. 
b. These options shall be added without using any of the programmable switch inputs on any of the panels.

8. [Each of the Panels [B] [C] [D] [E] [F] [G] [H] [J] [K] shall provide up to 32 programmable switch inputs, up to 48 programmable control relays, an RS232 interface module for access and configuration of any one of the set of ten control panels.  ]
a. Additional options for Panel B-K

1) Touch Panel user control interface 

2) Up to two motion sensors

b. These options shall be added without using any of the programmable switch inputs on any of the panels.

9. Each individual control relay shall provide an optional timer delay function with output timers for 30, 60, 90, 120, 180, 240 minutes.  

10. Each individual control relay shall provide an optional Warn Off (flash the lights) to inform the occupants of an impending Off command.  The Warn Off command shall provide a time delay duration of 5 extra minutes.  The occupants may exit the premises with adequate lighting or cancel the Warn Off by overriding the lighting zone.  This option occurs with all OFF commands except local overrides.

11. Each individual control relay shall permit lighting to be overridden ON.  The control system shall provide timed overrides assigned to specific relays.  Override times may be configured to 30, 60, 90, 120, 180, 240 minutes. Once the timed override expires the control system shall return the relays to their programmed state.  These overrides shall be hard-wired inputs.

12. Configuring the control system shall be through a Palm OS or PC based configuration software. The Palm OS device or PC may be connected to any panel in the control system via the RS232 interface module. The PC based configuration software shall permit either local configuration via the RS232 interface module or remote programming via an optional IP interface.  Descriptive information shall assist the user to employ the system without a programming manual.

13. Each control relay output shall provide a logic control function for logic (AND, OR) combination of inputs controlling the output relay. Logic AND control enables or disables an output relay based on Time of Day scheduling or any input in the system. Logic OR control provides forced ON control of an output relay by Time of Day scheduling or from any input in the system.  

B. HARDWARE FEATURES

1. OPERATOR INTERFACE
a. The control panel programming interface resides in firmware in the relay outputs and schedule assignments.  Systems that utilize blocking diode technology for relay assignments shall not be acceptable.

2. CONTACT INPUTS 
a. The control system shall permit up to 32 dry contacts (Digital/Switch Inputs) per control panel for override purposes.  Momentary 2 wire (toggle) inputs shall be supported.  Maintained contacts shall be supported as 2 wire (SPST) inputs.  Inputs shall be dry contacts (24 VDC @ 12 mA supplied to the inputs).  An input shall be software link-able to any number of relays for override control.

3. RELAY TYPE

a. The system shall utilize control relays, which are rated to 20 amps at 277 VAC max. The relays shall be mechanically held and are provided in groups of eight. The relays shall be rated for 1 million mechanical operations.  A limited 2-year warranty shall be provided on the individual relays.

b. The relays shall be modular in design and offer a manual override switch for manual control of the relay even in absence of control power to the relay module. The manual override switch should also provide visual indication of relay status.

c. Two relay outputs may be switched simultaneously for two pole loads.

d. The relay modules shall be approved for switching of different voltage levels or phases on adjacent relays. 

4. TIME CLOCK
a. The control system may contain a 4 channel time clock for individual time control of four groups of relays. The control system shall provide power for the time clock thereby eliminating any external power supply.  The time clock shall provide 372 Time of Day/holiday schedules for weekly, or 365 day programming.  

b. [Optionally the control system shall contain a 16 channel time clock. The control system shall provide power for the time clock thereby eliminating any external power supply.  The time clock shall provide 372 Time of Day/holiday schedules for weekly, or 365 day programming.  ]
c. The time clock shall utilize a battery back-up for the schedules and the operation of the quartz time clock. The time clock shall be protected against power interruptions lasting as long as ten years.  

5. [PHOTOCELL CONTROL
a. The control system shall provide for optional outdoor ambient light sensor.  The control system shall provide power for the sensor thereby eliminating any external power supply.  The sensor shall be for outdoor applications and provide the control signal to any number of output relays once the threshold is reached. The light sensor shall be connected to the panel with low voltage twisted pair. ]
6. [MOTION SENSOR
a. The control system shall provide option for up to two motion sensors per control panel.  The control system shall provide power for the sensor thereby eliminating any external power supply.  The sensor shall for indoor applications and provide the control signal to any number of output relays if motion is detected.  The motion sensors shall be connected to the panel with low voltage twisted pair. ]
7. MODULAR DESIGN
a. The control system shall employ an all modular design for easy addition of input or relay output modules.  The system shall still function if single modules should fail.

b. All connections for the switch inputs shall incorporate quick connect terminals.  The relay modules shall be designed for rapid field replacement or addition.  Systems that do not employ a modular design shall not be acceptable.

8. MEMORY BACK-UP
a. Any control system component with a microprocessor shall utilize non-volatile memory to store configuration data.  The data shall be protected against power interruptions lasting as long as ten years.  The data storage shall be entirely maintenance-free.  

9. CONTROL POWER SUPPLY
a. The control system shall incorporate the use of UL listed Class 2 power supply (120 VAC).  

10. OPTIONAL FORCED CONTROL OVERRIDE
a. Each relay module shall provide a forced control override of all relays in a relay module for service or priority override purposes. The forced control override may be applied via the Palm OS or PC based configuration tool, the optional Touch Display, or a dedicated forced control maintained three-way switch input. 

b. The forced control shall override provides “ALL ON”, "AUTO" and "ALL OFF" control of the relay modules.  The forced control shall operate all of the relays in the control relay module.  This forced control shall override and supersede all commands from other inputs when the forced control is in the “ALL ON or ALL OFF” position. 

c. The system shall remember the last command to the individual relays.  Upon returning the forced control override to the "AUTO" position, the relays shall return to the most recent command state.  This will occur even if the last command happened during the forced control override condition.

11. LOCKABLE ENCLOSURE
a. Each control panel shall be enclosed in a lockable, NEMA class 1 enclosure.  The enclosure shall be manufactured out of steel per UL916. Panels should offer a key lock option.
12. [ENCLOSURE WALL MOUNTING

a. The enclosure shall be for [surface] [flush] mounting.  ]
13. INTERNET PROTOCOL INTERFACE
a. The control system shall be capable of interfacing with a Local Area network using the Internet Protocol.

b. The system shall permit: Local Area Network (LAN), On-Site & Off-Site communications with the PC Set-up software. 

14. PC BASED SET-UP SOFTWARE 
a. PC based Set-up software shall enable any MS-Windows PC to configure any lighting control panel connected to the network.  The PC connection shall be an RS-232 direct connection to the lighting control panel at 9600 baud.  The software package shall allow individual panel programming to be executed locally or remotely through a Local Area Network (LAN) connection.  The configuration software shall permit the user to modify the control system configuration while the control system is in operation. The control system shall not be taken to an "OFF-LINE" mode.  This software package shall store all programmed data and archive for future use.

b. Software package shall permit the PC to be utilized for other functions (i.e. word processing, database, etc.) besides lighting control.  Systems that require an "on-line" dedicated computer for control system operation shall not be acceptable.

c. The following features shall be standard in the PC based Set-up software: 

1) Standard Software Features:

a) Real Time Relay Status Monitoring

b) Alpha-Numeric Descriptors

c) Configuration Modifications

d) Manual Relay Commands

2) File Maintenance

a) Archive Programs

b) Data Base Restoration

c) Uploading and Downloading of Configuration

15. CONFIGURATION INTERFACE (RS-232 PORT)
a. Each control panel shall provide an RS-232 module to permit configuration of any panel from any panel in the system using a Palm OS or PC based Set-up software.  The control panel shall provide an RS-232 module.  Configuration shall be permitted through either a local connection or remotely through a LAN connection.  PC software shall permit multiple file storage for data archival and for seasonal facility requirements. 

b. Operator commands may be issued directly from the Palm OS device or PC keyboard.

16. NETWORK (EIB)
a. The control system shall be capable of panel-to-panel communications over a hard-wired data network.  The network shall consist of twisted pair of wire utilizing the EIB communication standard.    The network shall support no less than 500 control panels.  This communication standard shall allow a maximum distance of 2100 feet for panel to panel communications.   The recommended wire is Belden #6230FE or equivalent.

17. Building Automation System (BAS) Interface:

a. The lighting control system shall be able to interface to systems that utilize the Internet Protocol on an Ethernet network, or the EIB standard. This will allow the BAS systems to control and retrieve the status of inputs and outputs in the lighting control system.
b. The lighting control system shall be able to interface to BAS with the use of OPC technology.

PART 3 -  EXECUTION

3.01 EQUIPMENT INSTALLATION AND DOCUMENTATION

A. INSTALLATION
1. The control system shall be installed and fully wired as shown on the plans by the installing contractor.  The contractor shall complete all electrical connections to all control circuits and override wiring.

B. DOCUMENTATION
1. The contractor shall provide accurate "as built" drawings to the owner for correct programming and proper maintenance of the Lighting Control system.  The "as built" shall indicate the load controlled by each relay and the relay panel number.

C. OPERATION AND SERVICE MANUALS
1. The factory shall supply all operation and service manuals.

3.02 PRODUCT SUPPORT AND SERVICE

A. FACTORY SUPPORT
1. Factory telephone support shall be available at no cost to the owner during the warranty period.  Factory assistance shall consist of solving programming or application questions concerning the control equipment.

3.03 SYSTEM INSTALLATION AND ACCEPTANCE

A. INSTALLATION
1. The contractor is responsible for complete installation of the entire system according to strict factory standards and requirements.  The following items shall constitute factory standards and requirements:

a. All system equipment shall operate in accordance with specification and industrial standard procedures.

b. An operational user program shall exist in the control system.  The program shall execute and perform all functions required to effectively operate the site according to the requirements.

c. A demonstration of program integrity during normal operation and pursuant to a power outage shall be performed.
d. Contractor shall provide a minimum of two training hours on the operation and use of the control system.  Additional support services shall be negotiated between the contractor and the building owner or manager.

3.04 WARRANTY

A. WARRANTY
1. Manufacturer shall supply a 2-year warranty on all hardware and software.  

2. The manufacturer shall provide customer service support 8 hours per day, Monday through Friday.  The manufacturer shall guarantee replacement of defective components.
END OF SECTION
September 7, 2004

[Project Name]
Programmable Lighting Control

16570 - 8
April 20, 2005

[Project Name]

Programmable Lighting Control 


16145-1

