SECTION 16269
VARIABLE FREQUENCY DRIVES
PART 1 -  GENERAL

1.01 DESCRIPTION

A. This specification is to cover a complete Variable Frequency Drive (VFD) consisting of a pulse width modulated (PWM) inverter designed for use on a standard NEMA Design B induction motor.

B. The drive and all necessary controls as herein specified shall be supplied by the drive manufacturer. The manufacturer shall have been engaged in the production of this type of equipment for a minimum of fifteen years.

1.02 QUALITY ASSURANCE

A. Referenced Standards:

1. Institute of Electrical and Electronic Engineers (IEEE)

a. Standard 519-1992, IEEE Guide for Harmonic Content and Control

2. Underwriters laboratories

a. UL508C

3. National Electrical Manufacturer’s Association (NEMA)

a. ICS 7.0, AC Adjustable Speed Drives

B. Testing:

1. All printed circuit boards shall be completely tested and burned-in before being assembled into the completed VFD. The VFD shall then be subjected to a computerized systems test (cold), burn-in and computerized systems test (hot). The burn-in shall be at 104 °F (4°C), at full rated load. All testing and manufacturing procedures shall be ISO 9001 certified.

C. Qualifications:

1. VFDs and options shall be UL listed as a complete assembly. VFDs and options shall be cUL listed as a complete assembly. VFDs and options shall be CE labeled as a component.

PART 2 -  PRODUCTS

2.01 VARIABLE FREQUENCY DRIVES

A. [The drive shall be manufactured by Siemens, be designed specifically for variable torque applications and shall be designated “SED2 Series” or approved equal by:
1. .

2. .  ]
B. The Variable Frequency Drives (VFDs) shall be solid state, with a Pulse Width Modulated (PWM) output. The VFD package as specified herein shall be enclosed in a NEMA 1 enclosure, completely assembled and tested by the manufacturer. The VFD shall employ a full wave rectifier (to prevent input line notching), Capacitors and Insulated Gate Bipolar Transistors (IGBT’s) as the output switching device. The drive efficiency shall be 97% or better at full speed and full load. Fundamental power factor shall be no less than 0.98 at all speeds and loads.
2.02 HARMONIC DISTORTION CONTROL
A. The VFD shall limit harmonic distortion reflected onto the utility system to a voltage and current level as defined by IEEE 519 for general systems applications.  This shall be accomplished by using drive components specifically designed to reduce harmonic distortion.  AC line reactors are required where their use will assist in reducing harmonic distortion.

B. Any harmonic calculations shall be done based on kVA capacity X/R ratio and the impedance of the utility transformer feeding the installation and the total system load.  The calculations shall be made with the point of the common coupling being the utility feeder.

C. Total harmonic distortion shall be calculated under the worst case conditions in the accordance with the procedure outlined in IEEE standard 519-1992.  Copies of these calculations are to be made available upon request.  The contractor shall provide any needed information to the VFD supplier.

D. The system containing the VFD shall comply with the 5% level of total harmonic distortion on line voltage and the line current limits as defined in IEEE 519-1992.

2.03 GENERAL
A. Input voltage [208-240] [380-480] [575-600] VAC +/- 10%, 3-phase, 48-63 Hz.
B. Undervoltage trip at rated input -35%, Overvoltage trip at rated input +30%.

C. Interrupt rating 65 kaic, suitable for use on a circuit capable of delivering not more than 10,000 RMS symmetrical amps, 480 V maximum.

D. Output Frequency 0 to 150 Hz. Operation above 60 Hz shall require programming changes to prevent inadvertent high-speed operation.

E. Environmental operating conditions: 0 to 4°C, 0 to 3300 feet above sea level, less than 95% humidity, non-condensing.

F. Enclosure shall be rated NEMA 1 or as specifically mentioned elsewhere.

2.04 FEATURES

A. All VFDs shall have the following standard features:

1. All VFDs shall have the same customer interface, including digital display and keypad, regardless of horsepower rating. The keypad is to be used for local control, for setting all parameters and for stepping through the displays and menus. The keypad shall be removable; it shall be capable of remote mounting; it shall have its own non-volatile memory. An optional keypad shall allow for uploading and downloading of parameter settings as an aid for start-up of multiple VFDs.

2. The keypad shall include Hand-Off-Auto membrane selections. When in “Hand”, the VFD will be started and the speed will be controlled from the up/down arrows. When in “Off”, the VFD will be stopped. When in “Auto”, the VFD will start via an external contact closure and the VFD speed will be controlled via an external speed reference. The drive shall incorporate “bump less transfer” of speed reference when switching between “Auto” and “Hand” modes.

3. The VFD’s shall utilize pre-programmed application macros specifically designed to facilitate start-up. The Application Macros shall provide one command to reprogram all parameters and customer interfaces for a particular application to reduce programming time.

4. The VFD shall have the ability to automatically restart after an overcurrent, overvoltage, undervoltage, or loss of input signal protective trip. The number of restart attempts, trial time and time between reset attempts shall be programmable.

5. The VFD shall be capable of starting into a rotating load (forward or reverse) and accelerate or decelerate to set point without safety tripping or component damage (flying start).

6. The VFD shall also be capable of DC injection braking at start to stop a reverse spinning motor prior to ramp.

7. The VFD shall be equipped with an automatic extended control power ride-through circuit, which will utilize the inertia of the load to keep the drive powered. Typical control power ride-through for a fan load shall be 2 seconds minimum.

8. If the input reference (4-20mA or 2-10V) is lost, the VFD shall give the user the option of either (1) stopping and displaying a fault, (2) running at a programmable preset speed, (3) hold the VFD speed based on the last good reference received, or (4) cause a warning to be issued, as selected by the user. The drive shall be programmable to signal this condition via a keypad warning, relay output and/or over the serial communication bus.

9. The customer terminal strip shall be isolated from the line and ground.

10. The drive shall employ current limit circuits to provide trip free operation:

a. The Slow Current Regulation limit circuit shall be adjustable to 150% (minimum) of the VFD's normal duty current rating. This adjustment shall be made via the keypad and shall be displayed in actual amps and not as percent of full load.

b. The Current Switch-off limit shall be fixed at 180% (minimum, instantaneous) of the VFD's normal duty current rating.

11. The overload rating of the drive shall be 110% of its normal duty current rating for 1 minute in every 10 minutes. The VFD shall have a low harmonics design where Total Harmonic Distortion (THD) shall not exceed 30% when measured at the VFD input terminals. Optional AC Input Reactors with a minimum of 3% impedance can be provided to protect the input diode bridge from incoming line transients or surges.

12. The VFD shall be capable of sensing a loss of load (broken belt / no water in pump) or high current mechanical sensing failure and signal the loss of load condition. The drive shall be programmable to signal this condition via a keypad warning, relay output and/or over the serial communications bus. Relay outputs shall include programmable time delays that will allow for drive acceleration from zero speed without signaling a false under load condition.

2.05 ADJUSTMENTS

A. All VFDs to have the following adjustments:

1. Four (4) programmable critical frequency lockout ranges to prevent the VFD from operating the load continuously at an unstable speed.

2. A custom PID preset for HVAC & fluid systems, allow a pressure or flow signal to be connected to the VFD, using the microprocessor in the VFD for the closed loop control. The VFD shall have 250 mA of 24 VDC auxiliary power and be capable of loop powering a transmitter supplied by others. The auxiliary power supply shall have overload and over current protection. The PID set point shall be adjustable from the VFD keypad, analog inputs, digital inputs, or over the communications bus.

3. Two (2) programmable analog inputs shall accept a current, voltage, or Ni 1000 sensor level input signal for speed reference or for reference and actual (feedback) signals for PID controller.

4. Analog inputs shall include a filter; programmable from 0.01 to 10 seconds to remove any oscillation in the input signal. The minimum and maximum values (gain and offset) shall be adjustable within the range of 0 - 20 ma and 0 - 10 Volts. Additionally, the reference must be able to be scaled so that maximum reference can represent a frequency less than 60 Hz, without lowering the drive maximum frequency below 60 Hz. Process variables shall be modifiable by math functions such as multiplication and division between the two signals (fan tracking), high/low select, as well as inverted follower.

5. Six (6) programmable digital inputs for maximum flexibility in interfacing with external devices. One digital input is to be utilized as a customer safety connection point for fire, freeze and smoke interlocks (Enable). Upon customer reset (reclosure of interlock) drive is to resume normal operation. These inputs can also be used to activate the set points of individual control loops.

6. Two (2) programmable analog output proportional to Frequency, Motor Speed, Output Voltage, Output Current, Motor Torque, Motor Power (kW), DC Bus voltage, Active Reference and other data.

7. Two (2) programmable digital relay outputs. The relays shall be rated for maximum switching current 8 amps at 24 VDC and 0.4 A at 250 VAC; Maximum voltage 300 VDC and 250 VAC; Continuous current rating 2 amps RMS. Outputs shall be full form C relay contacts; open collector outputs are not acceptable. Relays shall be capable of programmable on and off delay times.

8. Fifteen (15) programmable preset speeds.

9. Two independently adjustable accel and decel ramps. These ramp times shall be adjustable from 1 to 650 seconds.

10. The VFD shall Ramp or Coast to a stop, as selected by the user.

11. The following operating information displays shall be standard using an optional VFD digital display. All applicable operating values shall be capable of being displayed in engineering (user) units. All parameters viewed from the list below shall be capable of being displayed at all times. The display shall be in complete English words (alpha-numeric codes are not acceptable).

a. Output Frequency

b. Motor Speed (RPM, %, or Engineering units)

c. Motor Current

d. Calculated Motor Torque

e. Calculated Motor Power (kW)

f. DC Bus Voltage

g. Output Voltage

h. Heatsink Temperature ( 0°F)

i. Analog Input Values

j. Analog Output Value

k. Keypad Reference Values

l. Elapsed Time Meter (resettable)

m. kWh meter (resettable)

n. mWh meter

o. Digital input status

p. Digital output status

12. The VFD shall have the following protection circuits. In the case of a protective trip, the drive shall stop and announce the fault condition in complete words (alphanumeric codes are not acceptable):

a. Overcurrent trip 350% instantaneous (170% RMS) of the VFD's variable torque current rating.

b. Overvoltage trip 130% of the VFD's rated voltage

c. Undervoltage trip 65% of the VFD's rated voltage

d. Over temperature +90°C, Heatsink Temperature

e. Ground Fault either running or at start

f. Adaptable Electronic Motor Overload (I 2 t). The Electronic Motor Overload protection shall protect the motor based on speed, load curve and external fan parameter. Circuits, which are not speed dependant, are unacceptable. The electronic motor overload protection shall be UL Listed for this function.

13. Speed Command Input shall be via any of the following:

a. Keypad

b. Two Analog inputs, each shall be capable of accepting a 0-20mA, 4-20mA, 0-10V, 2-10V signal and a direct NI 1000 temperature sensor input.

c. Serial Communications

2.06 COMMUNICATIONS
A. The VFD shall have an RS-485 port as standard. The standard protocol shall be selectable between Siemens Building Technologies, Inc.  P1 (FLN) protocol and Johnson Controls Inc. N2 Metasys protocol.  There shall be an optional LON (LONMARK) interface and Modbus interface.

B. Serial communication capabilities shall include, but not be limited to, run-stop control; speed set adjustment, proportional/integral/derivative PID control (Set Point) adjustments, current limit and accel/decel time adjustments. The drive shall have the capability of allowing the DDC to monitor feedback such as process variable feedback, output speed/frequency, current (in amps), % torque, power (kW), kilowatt hours (resettable), operating hours (resettable), relay outputs, digital inputs and diagnostic warning and fault information. Additionally, remote (LAN) VFD fault reset shall be possible. A minimum of 15 field parameters shall be capable of being monitored.

C. The VFD shall allow the DDC to control the drive’s digital and analog outputs via the serial interface. The serial communications interface shall allow for DO (relay) control and AO (analog) control without being tied to a VFD function. In addition, all drive digital and analog inputs shall be capable of being monitored by the DDC system.

PART 3 -  EXECUTION

3.01 INSTALLATION

A. Installation shall be the responsibility of the mechanical contractor. The contractor shall install the drive in accordance with the recommendations of the VFD manufacturer as outlined in the installation manual.

B. Power wiring shall be completed by the electrical contractor. The contractor shall complete all wiring in accordance with the recommendations of the VFD manufacturer as outlined in the installation manual.

3.02 [START-UP

A. Certified factory start-up shall be provided for each drive by a factory authorized service center. A certified start-up form shall be filled out for each drive with a copy provided to the owner and a copy kept on file at the manufacturer.  ]
3.03 PRODUCT SUPPORT

A. Factory trained application engineering and service personnel that are thoroughly familiar with the SED2 drive products offered shall be locally available at both the specifying and installation locations.

3.04 WARRANTY

A. Warranty shall be 12 months from the date of certified start-up, not to exceed 18 months from the date of shipment from Siemens.
3.05 [OPTIONAL FEATURES – [Select as necessary] Optional features to be furnished and mounted by the drive manufacturer. All optional features shall be UL Listed by the drive manufacturer as a complete assembly.

A. Bypass Controller - Manual or automatic (selectable) transfer to line power via contactors. When in the “Drive” mode, the bypass contactor is open and the drive output contactor is closed. In the “Bypass” position, the drive output contactor is open and the bypass contactor is closed via Start/stop command. Start/stop via customer supplied maintained contact shall be Dry type 115V compatible and shall function in both the “Drive” and “Bypass” modes.  The design shall include single-phase protection in both the VFD and bypass modes.

1. Customer Interlock Terminal Strip – provide a separate terminal strip for connection of freeze, fire, smoke contacts and external start command. All external safety interlocks shall remain fully functional whether the system is in Hand, Auto, Drive or Bypass modes.

2. Automatic / manual bypass operation shall be selectable in the standard bypass design.

3. Door / cover interlocked disconnect switch which will disconnect all input power from the drive, bypass and all internally mounted options. The disconnect handle shall be through the door and be padlockable in the “Off” position.

4. Main input short circuit protection may be by motor rated fuses or circuit breaker. Expensive custom semi-conductor fuses will not be required.

5. Class 10 electronic motor overload protection shall be included in the bypass to protect the motor in bypass mode.

B. [NEMA 12 Enclosure] The optional NEMA 12 enclosure shall be UL Listed.  ]
END OF SECTION

April 20, 2005

[Project Name]

Variable Frequency Drives
16269-1

