Section 16442
PANELBOARDS

PART 1 -  general

1.01 SCOPE
A. The requirements of the Contract, Division 16 applies to work in this section. Panelboards as Specified and as shown on the contract drawings shall be furnished and installed by the Contractor.

1.02 RELATED SECTIONS

A. [Related Sections include the following:

1. Section 16410 - Enclosed Switches and Circuit Breakers
2. Section 16570 - Lighting Control

3. Section 16289 - Transient Voltage Suppression

4. Section 16950 - Short Circuit Analysis and Coordination Study

5. Section 16960 - Testing Requirements]
1.03 REFERENCES

A. The panelboards and circuit protection devices shall be manufactured and tested according to the latest applicable standards of the following agencies:

1. UL 50, Enclosures and Electrical Equipment

2. UL 67, Panelboards

3. UL 489, Molded Case Circuit Breakers and Circuit Breaker Enclosures

4. UL 943, Ground Fault Circuit Interrupters

5. NEMA PB1, Panelboards

6. NEMA PB1.1, General Instructions for Proper Installation, Operation and Maintenance of Panelboards Rated 600 Volts or less.

7. NEMA AB1, Molded Case Circuit Breakers and Molded Case Switches

8. Federal Spec W-P 115, Rev. C, Panel, Power Distribution

9. ANSI/NFPA 70, National Electric Code

10. ANSI/NEMA KS1, Enclosed and Miscellaneous Distribution Equipment Switches (600V)

1.04 SUBMITTALS

A. The manufacture shall provide the following information for review and evaluation by the Engineer:

1. Shop Drawings showing circuit breaker or fusible switch layout, dimensions, voltage, phasing, continuous current capacity, short circuit rating, Series rating is applicable.

2. Conduit entry location, cable termination sizes, mounting.

1.05 SUBMITTALS FOR CLOSEOUT

A. Manufacturer shall provide final, as- built drawings, recording the actual circuiting of panels.

B. Installation, Operation and Maintenance manuals shall also be supplied.

1.06 QUALITY CONTROL

A. The Panelboard manufacturer shall also be the manufacturer of the circuit breakers and fusible switches.

B. Manufacturer shall have produced similar electrical equipment for a minimum period of 10 years.

C. Products shall be listed by Underwriters Laboratories, Inc.

1.07 DELIVERY, STORAGE and HANDLING

A. Handle and store equipment in accordance with manufacturer’s Installation and Maintenance Manuals.  One (1) copy of this document to be provided with the equipment at time of shipment.

PART 2 -  products

2.01 MANUFACTURER(S)

A. [The panelboards shall be P-Series panelboards manufactured by Siemens Energy and Automation or pre-approved equal by: 

1.   ]
2.02 EQUIPMENT

A. Lighting And Power Distribution Panels (Standard)
1. Furnish Siemens Energy & Automation Lighting Panelboards, Type [P1].

2. NEMA PB 1, circuit breaker type.

B. Lighting and Power Distribution (Custom) for those applications requiring bus connected RC switches, Split bus, Special bussing size or material, Special wire connectors and other than standard size enclosures or voltages or systems. 

1. Furnish Siemens Energy & Automation Series Lighting Panelboards, Type [P2].

2. NEMA PB 1, circuit breaker type.

C. Distribution Panels
1. Furnish Siemens Energy & Automation Series Distribution Panelboards, Type [P3, P4 and P5].

2. NEMA PB 1, circuit breaker or fusible switch type.

2.03 COMPONENTS

A. Panelboards shall be as shown on the drawings. Refer to drawings for details regarding location of components, voltage and current rating of devices and other required details. Suitable for use as Service Entrance given compliance with NEC.

B. Panelboard Main Bussing : 

1. [Aluminum] [Copper] sized in accordance with UL 67 standards for temperature rise. 

a. Standard Lighting and Power Distribution Main Lug Panels to be rated 125A, 250A, 400A maximum. Main Circuit Breaker panels to be rated 100A, 125A, 225A, 250A, 400A. Main lugs shall be lay-in construction for panels up to 250 amps to facilitate connections. 

b. Custom Lighting and Power Distribution Main Lug Panels to be rated 125A, 225A, 250A, 400A and 600A maximum. Main Circuit Breaker panels to be rated 100A, 125A, 225A, 250A, 400A, and 600A.

c. Distribution Panel Main Lug Panels to be rated 250A, 400A, 600A, 800A and main breaker panels rated 250A, 400A and 600A maximum with branch breakers less than or equal to 250A for panels 24”wide X 7.75”deep (P3). For Main Lug panels rated 400A, 600A, 800A, 120A maximum and main switches rated 200A maximum with branch breakers less than or equal to 800amp, fusible switches less than or equal to 200A with box size of  32” wide X 10”deep (P4)  For Main lug panels rated and 400A, 600A, 800A and 1200 amp maximum and main panels rated 400A, 600A, 800A, and 1200A maximum and main switch rated 1200A maximum with branch breakers less than or equal to 1200 amps, fusible switches less than or equal to 1200A with a box size of 38” wide X 12.75” deep (P5). 

2. A [non-insulated] [insulated] [aluminum] [copper] equipment ground bar will be provided.
3. [Neutral bussing shall have a lug for each outgoing branch requiring a neutral connection; load side neutral connection lugs to be split with each side taking 50% of load neutral connections. [200 % neutrals shall be field upgradeable up to 400 amps on standard lighting and power distribution panels and provided for panels designated on drawings.]  ]
4. Standard lighting and power distribution panels shall be field convertible from Main Lug to Main Breaker with no increase in panel height. Field- addable mains (bussed connected) sub-feed breaker or feed-thru lug kits shall also be available, without utilizing any branch circuit space.

5. Interior shall be changeable from top to bottom feed and vice-versa, while maintaining readability of dead- front labeling on standard lighting and power distribution panels.

C. Enclosure

1. [Boxes shall be fabricated from galvanized, galvaneal steel or protected against corrosion per the requirements of NEMA 250 and UL 50. Box or panel interior shall have adjustable screws to provide easy alignment for flush mounted applications. Removable end walls to be [blank] [with KO’s]  ]
2. Trims

a. Trims for Lighting and Power distribution shall be [surface] [flush] as indicated on the drawings. It shall be fabricated from cold-rolled steel, painted with an ANSI-61 light gray finish and equipped with concealed hinges, flush lock and circuit directory cardholder. Trim shall have two separate supports designed to engage the box flange to stabilize and secure the trim during installation. Trim screws to be located behind the lockable door for tamper resistance. Optional trims may be hinged to the box, door in door.

b. Trims for Distribution Panels shall be [surface] [flush] as indicated on the drawings. It shall be fabricated from cold-rolled steel, painted with an ANSI-61 light gray finish. Optional trims may be hinged to the box, door in door.

D. Circuit Breakers

1. [Molded case circuit breakers shall be bolt-on devices only.  Plug-in type breakers are not acceptable.  Short circuit rating shall be amperes symmetrical based on [the smallest rating on any circuit breaker installed in the panel] [an integrated equipment short circuit rating] and as shown on the drawings, but not less than [10kaic] at 240 VAC or [14kaic] at 480 VAC.  ]
2. Molded case circuit breakers shall be thermal-magnetic, quick-make, quick-break, trip free. Multi-pole breakers shall be common trip. Branch connectors to be rated 200 amps for mounting two 100 amp breakers across from each other. Main breakers to be bus-connected to main bus bar and horizontally mounted. 

3. Provide circuit breaker accessories as indicated on the drawings or panel schedules.

4. Provide SWD rated breakers for all lighting branch circuits and UL Listed Type HACR for all air conditioning equipment branch breakers. 

5. [Integrated equipment short circuit ratings will be acceptable. A label shall be provided if Series ratings are applied showing the UL listed series combination of breakers.]

6. [Siemens Sentron Sensitrip III, Molded case, solid state circuit breakers shall utilize a micro-processor solid-state trip unit. Ampere ratings shall cover a continuous current range from 40 through 1200 amps.] All breakers shall have an interrupting rating of not less than [___] amperes RMS symmetrical at the system voltage, or as indicated on the drawings.

7. [Sentron Current Limiting circuit breakers shall provide inverse time delay, instantaneous circuit protection and also limit the I2t to a value less than the I2t of the one-half cycle wave of the symmetrical prospective current without fusible elements.] All breakers shall have an interrupting rating of not less than [___] amperes RMS symmetrical at the system voltage, or as indicated on the drawings.

8. [Fusible switches shall be quick-make, quick-break units utilizing the double-break principle of circuit interruption to minimize arcing and pitting and shall conform to the ratings shown on the plans. Each switch shall have an individual door over the front, equipped with a voidable interlock that prevents the door from being opened when the switch is in the “ON” position, unless the interlock is purposely defeated by activation of the voiding mechanism.]

9. [All switches have externally operated handles. Switches shall be equipped with NEC standard, Class R rejection type fuse holder[___] H, [___] K1, [___] K5, [___] RK1, [___] RK5, [___] T fuses of ampere rating and type as indicated on the plans suitable for application on a system with [___] ampere symmetrical available fault current.]

E. [Transient Voltage Surge Suppression]
1. If indicated on drawings, a TVSS shall be installed with a direct bus connection for low clamping and without utilizing any circuit breaker positions. It shall be listed in accordance with UL 67, 1283 and 1449. Designed and tested in accordance with ANSI/IEEE C62.45 and C62.41.

2. Surge capacity shall be [120kA] [160kA] [240kA] per phase Lighting Panelboards, Type [P1]. Surge Capacity shall be [160kA] [240kA] per phase for Distribution Panelboards, Type [P4] [P5]. EMI/RFI filtering shall be Active Tracking up to –50 db from 100 kHz to 100 MHz. Less than ½ nanosecond response time. Operating Frequency 47-63 Hz. Operating Temperature –40C to +65C.

3. Field-addable, bolt-on connection, into existing standard lighting panels with UL 1449 listing.

4. Factory installed TVSS units shall be available for mounting in unit space on Distribution panels. 

5. 5 year warranty with LED indicators for immediate status monitoring.  Audible alarm with silencing switch and test button.  

2.04 FINISH

A. Surfaces of the trim shall be properly cleaned and painted gray ANSI 61.

PART 3 -  execution

3.01 INSTALLATION

A. Install per manufacturer’s recommendations and contract documents.

3.02 FIELD TESTS

A. Check tightness of all accessible mechanical and electrical connections to assure they are torqued to the minimum acceptable manufacture’s recommendations.

B. Check all installed panels for proper grounding, fastening and alignment.

3.03 CLEANING

A. Remove debris from panelboards and wipe dust and dirt from all components.

B. Repaint marred and scratched surfaces with touch up paint to match original finish.

END OF SECTION

April 20, 2005


{Project Name}

Panelboards
16442-1

