                                 C


DIVISION 15





SECTION 15971





        		     


                                       CONTROLS FOR MECHANICAL EQUIPMENT








PART 1 � GENERAL








1.01	SUMMARY





A.	This Section specifies control requirements for mechanical equipment. The


	equipment involved is as follows:





     	1.	Air Handling Unit (AHU-1)


2.	Hot Water Three-Way Mixing Valve


3.	Return/Exhaust  Fan (RF-1)





B.	Control components required herein shall generally consist of the following, 


	but not be limited to:





1.	Local Control Panel � Complete with the following items:





Power On/Off Switch


Red Stop and Green Running Lights


Microprocessor-based, Programmable Controller


			Alarms and silencers


Manual Reset Button


                           Combination Starter(s) with Fusible Disconnect Switch(es) for AHU unit





Remote�mounted components for air handling unit including space sensor, discharge air sensor, outside air temperature sensor, return air enthalpy sensor, freezestat, enthalpy changeover controller, pressure differential switch, dampers with modulating motors and linkages, hot water control valve.  In addition, transformers, relays, switches, wiring and conduits shall also be furnished for the proper control operation of the equipment.





C.	Arrangement for control components is generally shown on the Contract Drawings.  The controls shall be capable of performing functions as stipulated in the "Control and Operation Requirements" as shown on the Contract Drawings.











1.02	REFERENCE





(NOT USED)











1.03	DESIGN AND PERFORMANCE REQUIREMENTS





Design and performance of components and methods specified herein shall comply with the applicable provisions of the codes, standards, and recommendations of the entities listed below.





American Society of Heating, Refrigerating and Air�Conditioning Engineers (ASHRAE)





National Fire Protection Association (NFPA)





Underwriters Laboratory (UL)





National Electrical Code (NEC)





In addition, specific provisions cited herein shall govern for the associated specific application.








1.04	QUALITY ASSURANCE





A.	Control components shall be state�of�the�art, manufactured by companies specializing in manufacturing control systems and devices.





B.	Control system shall be pre�wired and pre�tested in the shop.  Shop wiring and interfacing of control components shall be performed by control system manufacturer�authorized system distributor.





C.	Field wiring and installation of control systems shall be limited to connecting remote mounted components to the terminals in the Local Control  Panel, under the supervision of control system manufacturer�authorized technicians.





D.	Field test of the control system shall be performed by a control system manufacturer�authorized technician.





E.	The manufacturer�authorized system distributor shall have a local office staffed with trained, full�time employees who are capable of performing testing, inspection, repair and maintenance services for the life of the system.





F.	Local Control Panel shall bear the UL label.








1.05	DELIVERY, STORAGE, AND HANDLING





A.	The Local Control Panel shall be shop�wrapped and packaged against shock, dirt, and weather prior to shipping to the construction site.  Field installed components shall be delivered in manufacturer's original packages.





B.	The Local Control Panel and field installed components shall be stored in dry and clean spaces.











1.06	SUBMITTALS





  	A.	Submit the following in accordance with the requirements of "Shop Drawings, 	


		Catalog Cuts and Samples" of Division 1 � GENERAL PROVISIONS:





1.	Shop Drawings





	a.	Local Control Panel outline drawing showing the following:





Panel dimensions


Locations and arrangement of control components


Terminals with identifications for external connections





b.	Wiring diagram showing interfacing and interconnections of the Local Control Panel and remote mounted components. 





c.	Control schematic diagram with description of the control sequence for the control system.





2.	Catalog Cuts for all components showing the following:





Functions


Electrical Ratings


Wiring diagrams and requirements


Applications


Settings and adjustments


Testing procedures


Troubleshooting guides





B.	Submit six (6) copies of operation and maintenance manuals, including replacement and spare parts lists and troubleshooting guide.








1.07	TRAINING





     	Upon the completion of the installation, secure a technical representative of the control system manufacturer�authorized system distributor to provide one 8�hour day's training for Authority personnel. Location to be directed by the Engineer.








PART 2 � PRODUCTS








2.01	MANUFACTURERS





A.	Control system components used herein, with the exception of the Pressure Differential Switches, shall be products furnished and/or manufactured by one of the following manufacturers or approved equal:





Honeywell Inc.


Johnson Controls, Inc.


Robertshaw Controls, Inc.


Barber�Colman Co.





Non�standard, custom�programmed control system shall not be acceptable as an approved equal.





B.	Control system components used herein, with the exception of the Pressure Differential Switch, shall be catalog listed, off�the-shelf, regularly cross�listed by the above control system manufacturers as interchangeable components.  Manufacturers whose products are not listed by other manufacturers' catalogs as inter�changeable shall not be accepted.








2.02	CONSTRUCTION FEATURES





A.	Local Control Panel





1.	The panel shall be NEMA 4, wall�mounted and with hinged door front.





2.	Except for remote mounted control components, all components shall be internally mounted and fastened in the Local Control Panel, including:





*	Microprocessor-based, Programmable Controller


*	Relays


*	Low Voltage Transformers


*	Power On/Off Switch


*	Alarms and silencers


*	Manual Reset Button


			*	Combination Starter(s) with Fusible Disconnect Switch(es) for AHU unit





3.	The panel front door shall have identification plates for "Air handling Unit",  and shall be equipped with alarms, silencers, red and green lights for power on/off, and red stop and green running lights for AHU unit.


 


4.	Low Voltage Transformers shall be sized to match the load requirements of control components. An independent low voltage transformer shall be provide for the microprocessor-based programmable controller.





B.	Microprocessor-based Programmable Controller





The Controller shall be electronic, DDC, 24 VAC input, 4�20mA output, rated for 32 degree F to 122 degree F ambient, plug-in modular logic panel, capable of providing the following functions:





*	Measuring function with selectable ratio


*	On/Off operations


*	Modulation function


*	Limit Controls


*	Switching functions


*	Adjustable setpoints


*	Time programming


*	Interfacing





The Controller shall be equipped with panel mounted operator terminal to provide operator an easy access to messages and controller data.  The Controller shall be Honeywell Excel 80, or approved equal.








C.	Temperature Sensor For Discharge Air 





The sensor shall be averaging type temperature sensor, duct�mounted, platinum PTC, having an operating temperature range of 40 degree F to 180 degree F with an insertion length of 13 inch minimum.  It shall be Honeywell C7031J1068 or approved equal.





D.	Space Sensor  





		The sensor shall be wall mounted, platinum PTC, having an operating temperature


		range of -40 degree F to 100 degree F.  It shall be Honeywell C7130B1009 or


		approved equal.	





E.	Outside Air Temperature Sensor  





The sensor shall be wall mounted, platinum PTC, having an operating temperature range of -40 degree F to 110 degree F.  It shall be Honeywell C7031F1026 or approved equal.





F.	Freezestat





The freezestat shall be manual reset type, two SPST switches, 120 VAC, having a temperature range between 15 degree F to 55 degree F, with adjustable setpoint, UL listed, Honeywell Model L482A  or approved equal. 





G.	Enthalpy Changeover Controller





The enthalpy changeover controller shall be UL listed with solid state humidity sensing element and thermistor temperature sensing element, 24VAC, suitable for operation in -25 degree F to 125 degree F environment and have selectable setpoint.  It shall be capable of maximizing the use of outside air for cooling.





The enthalpy changeover controller shall be as supplied with Economizer Accessory Package manufactured by Carrier, or approved equal.





H.	Pressure Differential Switch





The switch shall be UL listed, diaphragm operated, designed for  monitoring fan operation, and shall be furnished with one (1) SPDT switch.  Motion of the diaphragm shall be restrained by a calibrated spring constructed of stainless steel materials that can be adjusted to set the exact pressure differential and shall be transmitted to the switch by means of a direct mechanical linkage.  It shall be designed for using 120 Volt/1 Phase/ 60 Hertz A.C. power supply.  Pressure differential switch shall be Model 1910-1 manufactured by Dwyer Instruments, Inc. or approved equal.








I.	Outside Air and Return Air Dampers, Motors, and Linkages


                     Dampers shall be low leakage type, opposed blade, roll-formed, galvanized steel


                     construction, 16 gage for damper blades and 13 gage for frame, fitted with nylon


                     bearings and stainless steel, spring-loaded, side seals.  Outside and return air 


                     dampers shall be as supplied with economizer accessory package manufactured by


                     Carrier or approved equal. Exhaust air damper shall be as manufactured by Ruskin


                     Model CD-50 or approved equal.





                     Motors shall be electronic, proportional, spring return, 120 VAC, used with 4-20 


                     mA input signal, 30 sec timing, having an adjustable stroke of 160 degrees, suitable


                     for ambient temperature between -40 degree F to 150 degree F. Outside and return


                     air damper motors shall be as supplied with economizer accessory package 


                     manufactured by Carrier or approved equal. Exhaust air damper motor shall be as


                     manufactured by Honeywell Model ML7285 or approved equal.





J.	Hot Water Control Valve for Hot Water Coil





The control valve shall be three-way, mixing, constant flow thru full plug travel, cast bronze body, metal-to-metal seat and disc, stainless steel stem, rated for 250 psig and 250 degree F water service. Valve motor shall be UL listed, proportional, 120 VAC, used with 4-20 mA modulating input signal, with integral transformer, spring return, suitable for -40 degree F to 150 degree F environment and capable of producing 60 lb-in torque.  Valve & valve motor shall be as manufactured by Honeywell or approved equal.





K.	Flow Switch





	Flow switch shall be UL listed, furnished with type 1 NEMA enclosure and one(1)


	SPDT auxiliary switch, design for maximum working pressure of 150 psig and maximum working temperature of 300 degree F, and shall have brass paddle. It shall be designed for using 120 volt/1 phase/60 Hertz  A.C. power supply. Flow switch  shall be Model FS4-3 manufactured by McDonnell & Miller or approved equal.





L.    Smoke Detector





         Smoke detector shall be duct mounted, designed for prevention of smoke 


         recirculation by shutting down the air handler system (AHU-1).  Smoke detector 


         shall be manufactured by Kele & Assoc. Model RW Series or approved equal.       








2.03	SHOP PAINTING





The Local Control Panels shall be painted per NEMA standard.








2.04	SHOP TEST





Upon the completion of fabricating the Local Control Panels, perform shop test in accordance with the recommendations of control system manufacturer.








PART 3 � EXECUTION








3.01	INSTALLATION





Field wiring and installation of the Local Control Panel and components shall be in accordance with the requirements as specified in Paragraph 1.04 � QUALITY ASSURANCE.








						END OF SECTION




















�PAGE  �








15971-� PAGE �1�











