G:\spec revision\M\15140M-Supports and Anchors.doc

SECTION 15140

SUPPORTS AND ANCHORS

1.00 GENERAL

1.01 PRINCIPal WORK IN THIS SECTION

A. Pipe and equipment hangers and supports.

B. Equipment bases and supports.

C. Sleeves and seals.

D. Flashing and sealing equipment and pipe stacks.

1.02 QUALITY ASSURANCE

A. Refer to General Provisions, Mechanical.

1.03 SUBMITTALS

A. Submit product data, drawings and calculations for the following items per the provisions of Division 1 and this Division’s General Provisions:

NOTE:
THIS SHOULD BE A NUMERICAL LIST OF DETAILED ITEMS THAT THE ENGINEER WISHES TO REVIEW.  IT SHOULD BE SPECIFIC AND NOT VAGUE.  A DATABASE WILL BE GENERATED FROM THIS LIST (FOR EACH INDIVIDUAL PROJECT) AND THE SHOP DRAWING DEPARTMENT WILL TRACK THE PERFORMANCE OF THE CONTRACTOR.  THIS WILL TAKE THE GUESS-WORK OUT OF WHICH SUBMITTALS HAVE BEEN SUBMITTED AND WILL ALLOW US TO PRO-ACTIVELY KEEP THE CONSTRUCTION PROCESS ON SCHEDULE.

KEEP IN MIND THAT ANYTHING REQUESTED IN THE GENERAL PROVISIONS SECTION WILL BE TRACKED UNDER THE GENERAL DIVISIONS FILE (BY THE SHOP DRAWING DEPARTMENT). KEEP 1.03 SIMPLE AND ONLY HAVE A 1.03 A AND NO 103 B.

IF ITEMS ARE LENGTHY, PROVIDE A ONE OR TWO WORD DESCRIPTION WITH A COLON, FOLLOWED BY THE MORE LENGTHY DESCRIPTION.

1. Product data:  Manufacturer’s catalog data including dimensions and installation instructions for all products proposed.  Provide load ratings for all hangers, supports and attachments.

2. Drawings:  Scale drawings of all specially fabricated supports and supports for all loads exceeding 1000 lbs.  Detail all supports from metal decks or concrete floors.

3. Calculations:  Required structural calculations by a licensed structural engineer.

NOTE:
OBTAIN AND INSERT PROPER SECTION NUMBERS.  COORDINATE WITH ARCHITECT.

1.04 PRODUCTS FURNISHED BUT NOT INSTALLED UNDER THIS SECTION

A. Section _______________:  PLACEMENT OF [INSERTS] [SLEEVES] IN CONCRETE FORMWORK.

B. Section ______________:  PLACEMENT OF ROOFING [PIPE] [DUCT] SUPPORTS.

C. Section ______________:  PLACEMENT OF EQUIPMENT ROOF SUPPORTS.

D. Section ______________:  PLACEMENT OF ROOF SLEEVES, VENTS, AND CURBS.

1.05 PRODUCTS INSTALLED BUT NOT FURNISHED UNDER THIS SECTION

A. Section ______________:  SUPPLY OF ROOFING [PIPE] [DUCT] [EQUIPMENT] SUPPORTS FOR PLACEMENT BY THIS SECTION.

1.06 RELATED SECTIONS

A. Section 03300 ‑ CAST‑IN‑PLACE CONCRETE: EQUIPMENT BASES.

B. Section 07270 ‑ FIRESTOPPING:  JOINT SEALS FOR PIPING AND DUCT PENETRATION OF FIRE RATED ASSEMBLIES.

C. Section 09900 ‑ PAINTING.

D. Section 15242 ‑ VIBRATION ISOLATION.

E. Section 15260 ‑ PIPING INSULATION.

F. Section 15280 ‑ EQUIPMENT INSULATION.

G. Section 15310 ‑ FIRE PROTECTION PIPING AND VALVES.

H. Section 15410 ‑ PLUMBING PIPING AND VALVES.

I. Section 15510 ‑ HVAC HYDRONIC PIPING.

J. Section 15520 ‑ STEAM AND STEAM CONDENSATE PIPING.

K. Section 15535 ‑ REFRIGERANT PIPING AND SPECIALTIES.

1.07 REFERENCES

A. ASME B31.1 ‑ POWER PIPING.

B. ASME B31.2 ‑ FUEL GAS PIPING.

C. ASME B31.5 ‑ REFRIGERATION PIPING.

D. ASME B31.9 ‑ BUILDING SERVICES PIPING.

E. ASTM F708 ‑ DESIGN AND INSTALLATION OF RIGID PIPE HANGERS.

F. MSS SP58 ‑ PIPE HANGERS AND SUPPORTS ‑ MATERIALS, DESIGN AND MANUFACTURER.

G. MSS SP69 ‑ PIPE HANGERS AND SUPPORTS ‑ SELECTION AND APPLICATION.

H. MSS SP89 ‑ PIPE HANGERS AND SUPPORTS ‑ FABRICATION AND INSTALLATION PRACTICES.

I. NFPA 13 ‑ INSTALLATION OF SPRINKLER SYSTEMS.

J. NFPA 14 ‑ INSTALLATION OF STANDPIPE AND HOSE SYSTEMS.

K. UL 203 ‑ PIPE HANGER EQUIPMENT FOR FIRE PROTECTION SERVICE.

L. ANSI B31.1 - CODE FOR PRESSURE  PIPING.

M. MANUFACTURED STANDARD SOCIETY DOCUMENT:  MSS-SP-58 and MSS-SP-69.

1.08 REGULATORY REQUIREMENTS

A. Provide an adequate pipe suspension system in accordance with recognized engineers practices, using standard commercially acceptable pipe hangers and accessories.

B. Supports for Sprinkler Piping: In conformance with NFPA 13.

C. Supports for Standpipes: In conformance with NFPA 14.

D. Where applicable codes require supports in excess of specifics herein, the Code shall govern.

E. Where thermal movement in pipe line occurs, hanger assembly shall support pipe line in all operating conditions.

2.00 PRODUCTS

2.01 MANUFACTURERS

A. Hangers, Inserts and Supports:

1. Fee and Mason.

2. ITT Grinnell Corporation.

3. Superstrut.

4. Tolco.

B. Pipe Protection and Thermal Hanger Shields:

1. Pipe Shields, Inc.

2. Elcen Metal Products Company.

3. Midland‑Ross Corp.: Superstrut.

4. Uni‑Grip.

5. Kin Line.

C. Expansion Shields:

1. ITT Phillips Drill Co.:  Red Head.

2. Hilti Fastening Systems.

3. Omark Industries, Inc.

4. Ramset Fastening Systems.

D. Miscellaneous Devices:

1. Kopty.

2. Wejit.

NOTE:
MAKE SURE THAT REQUIREMENTS INCLUDED IN 2.02 THROUGH THE END OF PART 2 DO NOT CONFLICT WITH MANUFACTURERS AND PRODUCTS SPECIFIED.

2.02 PIPE HANGERS AND SUPPORTS

NOTE:
SELECT ONLY HANGER AND SUPPORT TYPES APPLICABLE TO THIS PROJECT.

A. Model numbers are Superstrut, unless otherwise indicated.

 MACROBUTTON IndividualPipeHangers Delete if not required
B. Individual Pipe Hangers:

1. All hangers for pipes 2 inches and larger to be provided with means of vertical adjustment.

2. Cold pipe all sizes:  Clevis hanger, No. C710.

3. Hot pipe sizes up to 4 inches:  Clevis hanger, No. C710.

4. Hot pipe sizes above 6 inches:  Adjustable steel yoke and cast iron roll No. C729.

5. Cast iron pipe:  Hanger No. C‑710‑R.

6. Glass piping:  Plastic coated hanger No. C711‑P.

a. Use for other piping for corrosion protection or for cushioning. End of option
 MACROBUTTON MultipleHangers Delete if not required
C. Multiple or Trapeze Hangers:

 MACROBUTTON ChannelOption1 Select Channel Option 1
1. Factory channel:

a. 12 gauge thick steel.

b. Single or double section.

c. Electro‑chromate finish.

d. Strutnuts:  Series A‑100 or CM‑100.

e. Straps:  Series 702.

f. Other accessories.

g. No. A‑1200 or A‑1202. End of option
 MACROBUTTON ChannelOption2 Select Channel Option 2
2. Structural steel channels:

a. Back‑to‑back.

b. With spacers.

c. With U‑bolts. End of option
 MACROBUTTON ChannelOption3 Select Channel Option 3
3. Hot pipe sizes 6 in and larger:  Cast iron roll and stand; C728 or CR728. End of option End of option
 MACROBUTTON WallSupports Delete if not required
D. Wall Supports:

1. Pipe sizes up to 3 inches:  Steel bracket No. C738.

2. Pipe sizes 4 inches and larger:  Welded steel bracket C‑735.

3. Hot pipe sizes 6 inches and larger:

a. Welded steel bracket No. C739.

b. Adjustable steel yoke and cast iron roller No. C729. End of option
 MACROBUTTON VerticalSupports Delete if not required
E. Vertical Support:

1. Riser clamp Series C‑720.

2. At each floor unless otherwise indicated. End of option
 MACROBUTTON FloorSupport Delete if not required
F. Floor Support:

1. Hot pipe sizes up to 4 inches; cold pipe, all sizes:

a. Adjustable cast iron saddle No. R786.

b. Locknut nipple.

c. Floor flange.

2. Hot pipe sizes 6 inches and larger:  Adjustable cast iron roll and stand No. R‑730‑C. End of option
G. Thermal Hanger Shields.

1. Insulated pipe supports:

a. Insulated pipe supports shall be supplied and installed by the contractor on all insulated pipe and tubing.

b. All insulated pipe supports shall be load rated.  Load ratings shall be established by pipe support manufacturer based upon testing and analysis in conformance with the latest edition of the following codes:  ASME B 31.1, MSS SP-58, MSS SP-69, and MSS SP-89.

2. Approved insulated pipe support:

a. Pipe supported on rod hangers:

1) Equal to pipe shield A1000, A2000, A3000, A4000, and A9000.

b. Pipe supported on flat surfaces:

1) Equal to pipe shield A1000, A2000, A5000, A6000, and A7000 to A7400 Series.

c. Pipe supported on pipe rolls:

1) Equal to pipe shield A3000, A4000, A5000, A6000, and A8000 to 8400 Series.

d. Pipe Risers:

1) Equal to Pipe Shield Models E1000 to E1300 Series and E2000 to E2300 Series.

3. Insert to extend one inch beyond metal shield ends on following piping:

a. Refrigerant suction.

b. Chilled water.

c. Process cooling water.

d. (Other).

4. Shield lengths and gauges per manufacturer's published catalog recommendations.

5. Similar to Pipe Shields Incorporated.

H. Pipe Isolators:

1. Galvanized steel shell with felt padding.

2. Similar to:

a. Piping:  No. C715.

b. Tubing:  No. C716.

I. Insulated Pipe Strap:

1. 1/2 inch to 1 inch plumbing piping in wood frame construction.

2. Felt insulated.

3. Nailable pipe straps:

a. In lieu of other hangers and dielectric isolators.

4. Similar to Kopty.

2.03 STRUCTURAL ATTACHMENTS

A. Model Numbers are Superstrut, unless otherwise indicated.

B. Anchor Bolts:  Size as specified for hanger rods.

C. Concrete Inserts:

1. Malleable iron.

2. Place reinforcing steel through insert as recommended by manufacturer for recommended loads.

3. Equal to No. 452.

NOTE:
INCLUDE AS APPLICABLE FOR THIS JOB.  REVIEW HANGER ATTACHMENT METHODS THOROUGHLY.  THE FOLLOWING TYPES SHOULD APPLY TO MOST PROJECTS.  COORDINATE SPECIAL APPLICATIONS WITH MANUFACTURERS.

 MACROBUTTON BeamClamps Delete if not required
D. Beam Clamps:

1. All with U‑568 safety strap or equal.

2. All with locknuts on:

a. Set Screw.

b. Hanger rod.

3. Bottom flange attachment:

a. Loading 150 lb. and less:  U‑563 or equal.

b. Loading 150 lb. to 300 lb.:  U‑562 or equal.

c. Loading more than 300 lb.:  U‑560 or U-52, 521, or 522, depending on loading, or equal.

4. Top flange attachment:

a. Permitted only when bottom flange attachment cannot be used.

b. Loading 400 lb. and less:  M‑777 or equal.

c. Loading more than 400 lb.:  M‑778 or equal. End of option
 MACROBUTTON WeldedBeamAttachments Delete if not required
E. Welded Beam Attachments:

1. No. C‑780 or equal. End of option
 MACROBUTTON SideBeamBrackets Delete if not required
F. Side Beam Brackets:

1. No. 542. or equal. End of option
G. Hanger Rods:

1. ASTM A107.  Hot rolled steel.

2. ANSI B1.1 threads.

3. Threaded both ends, threaded one end, or continuous threaded.

H. Hanger Rod Fixtures:

1. Turnbuckles:

a. No. F‑112 or equal.

2. Linked Eye Rod:

a. Rod swivel.

b. No. E‑131 or equal.

3. Clevis:

a. No. F‑111 or equal.

NOTE:
CONFIRM ACCEPTABILITY OF POWDER ACTUATED ANCHORS WITH STRUCTURAL ENGINEER, CLIENT AND/OR REGULATORY AGENCIES.  DO NOT SPECIFY, UNLESS REQUESTED BY CLIENT, AND THEN ONLY WITH LIMITATIONS, SUCH AS IN CONCRETE WALLS ONLY, FOR EXAMPLE.

I. Powder Actuated Anchors:

1. Hardened steel stud with threaded shank:

a. Size of shank to match hanger rod size.

2. Use only with non‑shock loads.

3. Maximum load safety factors:

a. Static loads ‑ 5.

b. Vibratory loads ‑ 8‑10.

4. For concrete and steel.

a. Not to be used for brick or concrete block.

5. (Specify other material).

6. Omark "Drivit" or equal.

NOTE:
CONFIRM ACCEPTABILITY OF EXPANSION SHIELDS WITH STRUCTURAL ENGINEER, CLIENT AND/OR REGULATORY AGENCIES.

J. Expansion Shields:

1. Carbon‑steel anchors, zinc coated.

2. Stainless steel for corrosive atmospheres.

3. For normal concrete use:

a. Self‑drilling anchor.

b. Sleeve anchor.

c. Stud anchor.

4. For thin concrete use:

a. Wedge anchor.

5. For brick or concrete block use:

a. Sleeve anchor.

6. Maximum load safety factors:

a. Static loads ‑ 4.

b. Vibratory loads ‑ 8 ‑ 10.

c. Shock loads ‑ 8 ‑ 10.

7. Size to suit hanger rods.

8. ITT Phillips "Red Head" or equal.

K. Steel Deck Inserts:

1. Factory stud with:

a. Clip.

b. Spring.

c. Coupling.

2. ITT Phillips "Red‑Head" or equal.

L. Miscellaneous Metal:

1. Steel plate, shapes and bars:  ASTM A36.

2. Steel pipe columns:  ASTM A53, Schedule 40, black.

3. Bolts and nuts:  regular hexagon‑head type, ASTM A307, Grade A.

4. Lag bolts:  square head type, Fed. Spec. FF‑B‑561.

5. Plain washers:  round, carbon steel, Fed. Spec. FF‑W.92.

2.04 DUCT HANGERS AND SUPPORTS

A. See Section 15840:  DUCTWORK.

SELECT ONLY HANGER AND SUPPORT TYPES APPLICABLE TO THIS PROJECT.

3.00 EXECUTION

3.01 PIPE HANGERS, SUPPORTS AND GUIDES

A. General:

1. Assure adequate support for pipe and contents.

2. Prevent vibration or swaying.

3. Provide for expansion and contraction.

4. Supports of wire, rope, wood, chain, strap perforated bar or any other makeshift device not permitted.

5. Comply with applicable requirements at ANSI B31.1.0 and B31.2 for piping.

6. Support piping independently so that equipment is not stressed by piping weight of expansion.

7. See Section 15210:  VIBRATION ISOLATION AND SEISMIC CONTROL for hangers, guides, anchors and supports requiring vibration isolation units.

8. Hangers and supports shall have minimum safety factor of five (5), based on ultimate tensile or compressive strength, as applicable, of material used.

9. Prime coat exposed steel hangers and supports:

a. Hangers and supports located in crawl spaces, pipes shafts and suspended ceiling spaces are not considered exposed.

B. Horizontal piping, except as noted:

1. Adjustable clevis type and rod: 

a. All services at or below 250oF.

2. Rollers or slide bases:

a. Pipe stand, bracket, trapeze or other equivalent structural support.

b. For following services, 2 inches and larger:

1) High pressure steam.

2) High pressure condensate return.

c. Rollers not required where spring hangers are called for.

3. Trapeze hangers:

a. Not permitted for:

1) Steam and condensate piping.

2) Fire and sprinkler piping.

3) Chemical waste drain piping.

4) Piping with different expansion requirements not permitted on common trapeze.

b. Guide individual pipes on trapezes with 1/4 inch U‑bolt or Superstrut 702 pipe clamp.

1) Install thermal hanger shield at each support point.

4. Galvanized sheet metal shields between hangers and PVC piping.

5. Threaded steel rods:

a. 2 inch vertical adjustment with 2 nuts each end for positioning and locking.

b. Size to 12 inches IPS:

Pipe, IPS
Rod

to 2 in. 
3/8 in.

2‑1/2 in. and 3 in. 
1/2 in.

4 in. 
5/8 in.

6 in. and 8 in. 
3/4 in.

10 in. and 12 in. 
7/8 in.

c. Size above 12 inches IPS and multiple pipe standards:  safety factor of 5 on ultimate strength on area.

d. For double rod hangers:  1 size smaller than above.

6. For drainage piping buried below slab on grade see Section 15010:  GENERAL PROVISIONS, MECHANICAL.

C. Vertical piping:

1. Base support:

a. Base elbow or welded equivalent.

b. Bearing plate on structural support.

2. Guides at every third floor but not to exceed:

a. 25 feet for piping to 2 inches.

b. 36 feet for piping 2‑1/2 inch to 12 inches.

c. 50 feet for piping 14 inches and larger.

3. Top support:

a. Special hanger or saddle in horizontal connection.

b. Provisions for expansion.

4. Intermediate supports:  steel pipe clamp at floor:

a. Bolted and welded to pipe.

b. Extension ends bearing on structural steel or bearing plates with spring supports rated for load and positioned for expansion.

5. For multiple pipes:  coordinate guides, bearing plates and accessory steel.

D. Horizontal insulated piping:

EDIT TO SUIT JOB REQUIREMENTS.  INCLUDE ONLY REFERENCES DIRECTLY AFFECTING WORK OF THIS SECTION.

1. Install thermal hanger shields for all types of supports.

2. See Section 15260:  MECHANICAL PIPING INSULATION for insulation connection to shields.

E. Vertical insulated piping:

1. Install thermal hanger shields at guides.

2. See Section 15260:  MECHANICAL PIPING INSULATION for insulation connection to shields.

F. Install Pipe isolators between hangers and:

1. Insulated copper tubing.

2. Glass drain piping.

3. Wherever any pipe requires sound and vibration isolation.

G. Plumbing Walls:

1. Small plumbing piping in walls may be supported from steel waste and vent piping with WEJ‑IT "Adjusto‑Spacer System" components in lieu of other hangers and isolators.

2. Steel support components shall be separated from copper piping with plastic tape.

H. Spring Supports for Piping:

1. See Section 15242:  VIBRATION ISOLATION.

2. Minimum Static Deflection:  1 inch:

a. Unless otherwise indicated.

I. Miscellaneous Steel:

1. Provide miscellaneous steel members, beams, brackets, etc., for support of work in this division unless specifically included in other divisions.

INCLUDE AS APPLICABLE FOR THIS JOB.

 MACROBUTTON PipeTunnelSupports Delete if not required
J. Pipe Tunnel Supports:

1. Install structural framing to support piping and ducts as indicated on drawings:

a. Support weight of pipes.

b. Withstand thermal expansion and seismic bracing loads.

c. Include required bracing in all directions.

d. Size members for all loads with safety factor of five (5), based on ultimate strength.

2. Space framing as specified for pipes having minimum spacing.

3. Provide columns with top fittings to permit differential motion between floor and ceiling slabs.

4. Framing may be one of methods listed below, or combination of both as required:

a. Fabricated from structural shapes:

1) Submit calculations for design.

b. Formed channels with fittings similar to Superstrut:

1) Submit manufacturer's calculations for installation. End of option
3.02 PIPE SUPPORT SPACING

INCLUDE AS APPLICABLE FOR THIS JOB.  THE FOLLOWING MAXIMUM SPACING IS RECOMMENDED; EDIT AS REQUIRED IF OTHER CODES, CLIENT REQUIREMENTS, ETC., CALL FOR CLOSER SPACING.  REVIEW PLASTIC PIPING SUPPORTS WITH DEPARTMENT CHIEFS.  THEY MAY REQUIRE CONTINUOUS SUPPORTS.

A. Maximum spacing for horizontal piping:

Type of Pipe
Size
Maximum Spacing 

 MACROBUTTON Steel Delete if not required
Steel
1 in. to 1-1/4 in.
 7 ft.

1-1/2 in.
 9 ft.

2 in.
10 ft.

2-1/2 in.
11 ft.

4 in.
14 ft.

5 in.
16 ft.

6 in.
17 ft.

8 in.
19 ft.

10 in.
22 ft.

12 in.
23 ft.

14 in.
25 ft.

16 in.
27 ft.

18 in.
28 ft.

20 in.
30 ft.

24 in.
32 ft. End of option
 MACROBUTTON BrassorCopper Delete if not required
Brass or copper
3/4 in. and smaller
 5 ft.

1 - 1‑1/4 in.
 6 ft.

1‑1/2 ‑ 3 in.
 8 ft.

4 in. and larger
10 ft. End of option
 MACROBUTTON BellandSpigot Delete if not required
Bell and Spigot
All
10 ft.

(Notes 1, 2, 3) End of option
 MACROBUTTON HublessCI Delete if not required
Hubless C.I.
All
10 ft.

(Notes 2,4) End of option
 MACROBUTTON RigidPlastic Delete if not required
Rigid Plastic
3/4 in. and smaller 
 3 ft.

(Note 2)
1 ‑ 1‑1/2 in.
 4 ft.

2 ‑ 3 in.
 6 ft.

4 in. and larger
 8 ft. End of option
 MACROBUTTON Glass Delete if not required
Glass
All
 8 ft. End of option
NOTE:
THESE NOTES MUST BE INCLUDED IN THE FINISHED SPECIFICATION.  EDIT OUT THOSE NOT REQUIRED.

B. Spacing Notes:

1. Typical of cast iron and duriron.

2. Not less than one support per joint.

3. Support to be with 18 inches of hub or joint.

4. Support to be placed on or immediately adjacent to coupling.

Additional supports at:

5. Changes in direction.

6. Branch piping and runouts over 5 feet.

7. Concentrated loads due to valves, strainers and other similar items.

8. At valves 4 inches and larger in horizontal piping.

a. Support piping on each side of valve.

9. Brace hubless piping to prevent horizontal and/or vertical movement.

C. Parallel piping on trapezes:

1. Maximum spacing to be that of pipe requiring closest spacing.

NOTE:
INCLUDE AS APPLICABLE FOR THIS JOB.  SPECIFY OTHER AGENCY IF NFPA IS NOT APPLICABLE TO THIS PROJECT.

 MACROBUTTON Standpipes Delete if not required
D. Support standpipes and fire sprinkler piping in accordance with NFPA. End of option
3.03 ATTACHMENT TO STRUCTURE

NOTE:
CONFIRM INSTRUCTIONS TO INSERT LOCATIONS IN WAFFLE SLABS AND BEAMS, PRECAST ELEMENTS, ETC.

A. Concrete:

1. Use inserts for suspending hangers from reinforced concrete slabs, walls and sides of reinforced concrete beams wherever practicable.

2. Set inserts in position in advance of concrete work. 

3. Provide reinforcement rod in concrete for inserts carrying: 

a. Pipe over 4 in. 

4. Where rod size exceeds 7/8 in. diameter, or where load exceeds insert rating, use the inserts with a trapeze type member connecting member below concrete.

5. Where concrete slabs form finished ceiling, finish inserts flush with slab surface.

6. Where inserts are omitted install hangers with expansion shields.

NOTE:
INCLUDE AS APPLICABLE FOR THIS JOB.  IN REMODELING EXISTING BUILDINGS EXPANSION SHIELDS MAY NOT BE PERMITTED BECAUSE OF UNCERTAINTY AS TO THE QUALITY OF THE OLD CONCRETE AND ITS HOLDING ABILITY.  IN SUCH CASES, THE FOLLOWING METHOD MUST BE USED.  COORDINATE WITH CONDITIONS ON TOPE OF THE SLABS.  EDIT THE FOLLOWING TO SUIT JOB CONDITIONS.

 MACROBUTTON ThroughDeckSupport Delete if not required
7. Through-deck support:

a. Drill through concrete slab from below.

b. Provide rod with recessed square steel plate and nut above slab. End of option
INCLUDE AS APPLICABLE FOR THIS JOB.  SEE NOTE IN PART 2 REGARDING POWDER DRIVEN INSERTS.

 MACROBUTTON PowderDrivenInserts Delete if not required
8. Where permitted by structural engineer and regulating agencies powder actuated anchors or expansion shields may be used in lieu of inserts:

a. In bottom of thick slabs.

b. In thin slab construction, only in sides of beams. End of option
 MACROBUTTON PrecastConcrete Delete if not required
9. Pre-Cast Concrete:

a. Use pre‑set inserts.

b. Where inserts are not available, field drill through beam or joists at locations as directed by Architect.

c. Through bolt side beam bracket to beam or joist. End of option
 MACROBUTTON PouredinPlaceConcrete Delete if not required
10. Poured-in-Place Concrete:

a. With metal form or underdeck.

b. Before concrete is poured:

1) Field drill hole through metal deck.

OPTION!
SELECT APPLICABLE OPTION FROM THE FOLLOWING LISTINGS:

 MACROBUTTON ConcreteInsertsOption1 Select Concrete Inserts Option 1
2) Provide bearing plate, nut and locknut on rod. End of option
 MACROBUTTON ConcreteInsertsOption2 Select Concrete Inserts Option 2
3) Install factory-made steel deck inserts specified hereinbefore. End of option
c. After concrete is poured:

1) Install hangers with expansion shields. End of option
B. Steel Beam Anchors:

1. Approved beam or channel clamps.

2. Do not cut or weld to structural steel without permission of structural engineer.

NOTE:
COORDINATE WITH PROJECT DIRECTOR AND STRUCTURAL ENGINEER.

3. Other methods as detailed on drawings.

C. Steel Deck Anchors:

1. Concrete filled:  as specified above.

NOTE:
COORDINATE WITH CONDITIONS ON TOP OF SLAB BEFORE SPECIFYING THIS METHOD.

2. Decking without concrete:

a. Through rod Support:

1) Weld to square plate, 1/4 inch thick.

2) Plate to distribute load over minimum of two full cells.

3) Coordinate with floor layouts to clear cells with wiring.

D. Timber Anchors:

1. Approved side‑beam brackets:

a. Secure with lag‑screw in middle third of wood beam or joist.

2. Direct vertical tension:

a. Through bolt with washer on top.

NOTE:
COORDINATE WITH PROJECT DIRECTOR AND STRUCTURAL ENGINEER.

3. Other methods as detailed on drawings.

E. Side Wall Supports:

1. Concrete walls:

a. As specified for hangers.

NOTE:
ARRANGE FOR PROPER STRUCTURAL BACKING TO RECEIVE ATTACHING BOLTS, ETC.

2. Stud Walls:

a. Toggle bolts.

b. Studs welded to structural studs.

c. Lag screws into wood backing.

d. Other methods:

F. Support Spreaders:

1. Install spreaders spanning between structural members when hangers fall between them, and hanger load is too great for slab or deck attachment.

2. Spreaders may be one of methods listed below, or combination of both as required:

a. Fabricated from structural channel:

1) End fittings bolted or welded.

2) Secure to structural members:

a) As required by construction.

b) As approved by Structural Engineer.

b. Formed channels with fittings, similar to Superstrut:

1) Submit manufacturer's calculations for installation.

3.04 DUCT HANGERS AND SUPPORTS

A. See Section 15840:  DUCTWORK.

NOTE:
REVIEW THE WORK INCLUDED IN PARAGRAPH 1.01.  FOR EACH ITEM LISTED THERE MUST BE A CORRESPONDING PARAGRAPH IN PART 2 AND/OR PART 3.

REVIEW THE INDEX ‑ LIST OF ARTICLE TITLES.

END OF SECTION

G:\spec revision\M\15140M-Supports and Anchors.doc
MASTER MECHANICAL
SECTION 15140 - 22
SPECIFICATION
SUPPORTS AND ANCHORS


REV. 05/00


