C:\Ida's Folder\Spec Revisions\Mechanical Reformatted\15624M.DOC

SECTION 15624

DIRECT FIRED AIR UNITS

NOTE:
THIS IS NOT A MASTER.  DETAILED EDITING IS REQUIRED FOR EACH PROJECT.
1.00 GENERAL

1.01 PRINCIPAL WORK IN THIS SECTION

A. Direct fired make-up air heater.

B. Cooling coil section and compressor-condenser unit.

C. Service platform.

D. Controls.

1.02 SUBMITTALS

A. Product Data:  Catalog cuts giving dimensions, duct and service connections, accessories, controls, and electrical nameplate data.

1.03 OPERATION AND MAINTENANCE DATA

A. Include manufacturer's descriptive literature, operating instructions, installation instructions, maintenance and repair data, and parts listing.

1.04 EXTRA MATERIALS

A. Provide [two] [_____] set of filters.

2.00 PRODUCTS

2.01 MANUFACTURERS

A. [___________________________________] Model [__________.]

B. [___________________________________] Model [__________.]

C. [___________________________________] Model [__________.]

2.02 MANUFACTURED :UNITS

A. Unit: [Dual volume] [outdoor] [indoor] unit[.] [with refrigeration package.]

B. Construction and Ratings: In accordance with ARI, and ANSI/UL.  Testing:  ASHRAE.

C. Performance Ratings: Energy Efficiency Rating (EER) not less than requirements of ANSI/ASHRAE.

2.03 FABRICATION

A. Casing and Components: Steel Panels, 18 gage (1.2 mm) reinforced with structural angles and channels to ensure rigidity; access panels to burner and blower motor assemblies from either side of unit.

B. Observation Port: On burner section for observing main and pilot flames.

C. Insulation: Neoprene faced glass fiber insulation one in. (25 mm) thick on [inlet components to burner profile plate.] [complete unit.]

D. Finish: Heat resistant baked enamel.

E. Suspended Installations: Service platforms complete with handrails and access ladder.

F. Outdoor Installation: Weatherproofed casing, with intake louver or hood.

2.04 FILTERS

A. Filter:  Removable [one in.] [2 in.] thick [high velocity permanent] [glass fiber disposable] filters in metal frames.

2.05 BURNERS

A. Assembly: For [natural] [propane] gas, capable of modulating turn down ratio of 25:1, including electric modulating main gas valve, motorized shut down valve, main and pilot gas regulators, pilot electric gas valve, manual shut-off valve and pilot adjustment valve.

B. Pilot: Electrically ignited by spark rod through high voltage ignition transformer and supervised.

C. Damper: Motorized with end switch to prove position before burner will fire.

2.06 FAN

A. Fan: Statically and dynamically balanced centrifugal fan mounted on solid steel shaft with heavy duty self-aligning pre-lubricated ball bearings and V-belt drive with matching motor sheaves and belts.

2.07 CONTROLS

A. Controls: Pre-wire unit for connection of power supply. Field wiring from unit to remote control panel makes unit operative.

B. Remote Control Panel: On-off-[auto] switch, [summer-winter switch,] indicating lights for supply fan, [exhaust fan,] pilot operation, burner operation, clogged filter indication and [lockout indication].

C. Interlocks: Unit to start when exhaust fan is running. Burner to operate when flow switch located in exhaust duct proves flow.  [Exhaust fan speed control with inlet damper and burner profile damper to provide dual volume air capacity.] [Exhaust fans operate with inlet damper and burner profile damper to provide dual volume operation.]

D. Fan Discharge Thermostat: Controls modulating gas valve to maintain supply air temperature.  [Provide remote discharge thermostat adjustment [within 20 ft of unit.] [in excess of 20 ft of unit.]] [Provide room thermostat to reset discharge thermostat minimum of three temperature levels.]

E. Timer: Operates fan system [off at night.] [on low volume at night.]

F. Carbon Monoxide Monitoring System: Operates fan on high volume when pre-determined carbon monoxide concentration is detected.

G. Safety Controls: Sense correct air flow before energizing pilot and sense pilot ignition before activating main gas valve.

H. Manual Reset Low and High Limit Controls:  Maintain supply air temperature between set points and shut fan down if temperatures are exceeded.

I. Purge Period Timer:  Automatically delays burner ignition and bypass low limit control.

2.08 REFRIGERATION PACKAGE

A. Evaporator Coil:  Copper tube aluminum fin coil assembly with galvanized drain pan and expansion valve.

B. Compressor:  [ARI] hermetic, 3600 rpm maximum resiliently with positive lubrication, crankcase heater, high pressure control, motor overload protection, service valves and drier.

C. Condenser:  [ARI] aluminum fin and copper tube coil, direct drive axial fan resiliently mounted, galvanized fan guard.

D. Operating Controls:  Low voltage, adjustable room thermostat controls compressor and condenser fan to maintain room temperature setting.

3.00 EXECUTION

3.01 INSTALLATION

A. Install in accordance with manufacturer's instructions.

B. Install to NFPA.

C. Install to ANSI Z223.1.

END OF SECTION

\\LAO-01\DATA\PUBLIC\MASTER\WRD97SPC\M\15624M.DOC
MASTER MECHANICAL
SECTION 15624 - 1
SPECIFICATION
DIRECT FIRED AIR UNITS

REV. 12/99

