C:\Ida's Folder\Spec Revisions\Mechanical Reformatted\15659M.DOC

SECTION 15659

ROTARY REFRIGERANT COMPRESSORS

1.00 GENERAL

1.01 PRINCIPAL WORK IN THIS SECTION

A. Rotary compressor units.

B. Internal piping and accessories.

C. Controls and control panel.

D. Motor controllers.

1.02 SUBMITTALS

A. Product data:  Catalog cuts giving rated capacities, weights, accessories, and electrical nameplate data.

1.03 OPERATION AND MAINTENANCE DATA

A. Include start-up instructions, maintenance instructions, parts lists, controls, and accessories.

NOTE:
PARTS 2 AND 3 REQUIRE REWRITING FOR ROTARY COMPRESSORS.  DO NOT USE UNTIL REWRITTEN.
2.00 PRODUCTS

2.01 MANUFACTURERS

A. [______________________________] Product [__________.]

B. [______________________________] Product [__________.]

C. [______________________________] Product [__________.]

2.02 MANUFACTURED UNITS

A. Compressor Units:  Rotary compressor and motor, with [cylinder unloaders,] crankcase heater, suction and discharge service valves, vibration isolators, and control panel.

B. Construction and Ratings: In accordance with ARI and ANSI/UL.  Testing shall be in accordance with ASHRAE.

C. Performance:   Ratings: Energy Efficiency Rating (EER) [and Coefficient of Performance (COP)] not less than prescribed by ANSI/ASHRAE.

D. Performance:  Not more than 1.1 KW/ton.

2.03 ROTARY COMPRESSORS

A. Compressors: Statically and dynamically balanced crankshaft, spring loaded discharge valves, internal pressure relief valve, suction service valve, discharge muffler.  Install in welded steel shell, with integral suction accumulator, internally mounted on spring vibration isolators.

B. Lubrication System: Oil charging valve[,] [oil level sight glass, oil filter, and magnetic plug or strainer,] arranged to ensure adequate lubrication during starting, stopping, and normal operation.

C. Capacity Reduction Equipment: Electrically actuated suction valve unloaders with replaceable solenoid valves, starting compressor unloaded.

D. Motor: [Constant speed] [Two speed] [1800] [3600] [3600/1800] rpm, suction gas cooled[,] [with two winding thermostats providing overheating protection,] designed for across-the-line starting, with starter.

E. Crankcase Heater: To evaporate refrigerant returning to crankcase during shut down, energize [continuously.] [when compressor is not operating.]

2.04 CONTROLS

A. On compressor, mount steel control panel, containing power and control wiring, [disconnect switch,] factory wired with single point power connection.

B. Provide [across-the-line] [part winding] [__________] starter, non-recycling compressor overload, starter relay, control power transformer or terminal for controls power[,][.] [and terminal strip for connection to interface equipment.] Provide manual reset current overload protection.

C. Provide the following devices on control panel face:

1. Compressor run light.

2. Start-stop switch.

3. Control power fuse or circuit breaker.

4. Demand limit switch.

5. Elapsed time meter.

6. Crankcase heater start-stop switch and light.

D. Provide high discharge pressure switch, low suction pressure switch, and oil pressure switch safety controls [with pilot lights] arranged so that operating any one will shut down machine and require manual reset.

E. Provide the following operating controls:

1. Multi-step suction pressure controller which activates cylinder unloaders.

2. Timer prevents compressor from short cycling.

3. Part winding start timer.

4. Periodic pump-out timer to pump down on high suction refrigerant pressure.

F. Provide pre-piped gage board with pressure gages for suction and discharge refrigerant pressures, and oil pressure.

3.00 EXECUTION

3.01 INSTALLATION

A. Install in accordance with manufacturer's instructions.

B. Provide for connection to electrical service.

C. Align compressor package on steel or concrete foundations.

D. Install units on [rubber-in-shear] vibration isolation.

E. Provide connection to refrigerant piping.

F. Arrange piping for easy dismantling to permit tube cleaning.

3.02 MANUFACTURER'S FIELD SERVICES

A. Prepare start systems under provisions of Section [01600.] [01650.]

B. Supply service of factory trained representative for a period of [_____] days to supervise testing, dehydration and charging of machine, start-up, and instruction on operation and maintenance to Owner.

C. Supply initial charge of refrigerant and oil.

END OF SECTION

G:\PUBLIC\MASTER\WRD97SPC\M\15659M.DOC
MASTER MECHANICAL
SECTION 15659 - 1
SPECIFICATION
ROTARY REFRIGERANT COMPRESSORS

REV. 12/99

