C:\Ida's Folder\Spec Revisions\Mechanical Reformatted\15730M.DOC

SECTION 15730

LIQUID COOLERS

NOTE:
DO NOT USE THIS SECTION UNTIL IT IS REWRITTEN SPECIFICALLY FOR LIQUID COOLERS.

1.00 GENERAL

1.01 PRINCIPAL WORK IN THIS SECTION

A. Liquid cooler.

B. Controls.

C. Ladder and handrails.

D. Circulating pump.

E. Sound attenuators.

F. Discharge hood.

1.02 SUBMITTALS

A. Product data:  Catalog cuts giving rated capacities, dimensions, weights and point loadings, accessories, required clearances, electrical requirements, location and size of field connections and schematic indicating capacity controls.

B. Certify performance, based on CTI and submit performance curve plotting leaving water temperature against wet bulb temperature.

1.03 OPERATION AND MAINTENANCE DATA

A. Include start-up instructions, maintenance data, parts lists, controls, and accessories.

B. Include cleaning methods and cleaning materials recommended.

1.04 DELIVERY, STORAGE, AND HANDLING

A. Factory assemble entire unit.  For shipping, disassemble into as large as practical sub-assemblies so that minimum amount of field work is required for re-assembly.

B. Store and protect products under provisions of Section [01600.] [01620.]

C. Comply with manufacturer's installation instructions for rigging, unloading, and transporting units.

1.05 WARRANTY

A. Provide [five] [_____] year warranty under provisions of Section [01700.] [01740.]

B. Warranty: Include coverage for [liquid cooler package] [fan drive.] [motor.] [pan, casing and cooler coil.] [labor.] [and] [materials.] [only.]

1.06 EXTRA MATERIALS

A. Submit maintenance materials under provisions of Section [01700.] [01750.]

B. Provide one set of matched fan belts, [twelve] [_____] spray nozzles, one spare gasket for each access door, one valve seat for each make-up valve, one strainer screen, one float, one pump seal, and one set of pump gaskets, under provisions of Section [01700.] [01750.]

2.00 PRODUCTS

2.01 MANUFACTURERS

A. [__________________________________] Product [__________.]

B. [__________________________________] Product [__________.]

C. [__________________________________] Product [__________.]

2.02 MANUFACTURED UNITS

A. Provide units for [outdoor] [indoor] use, factory assembled, sectional, counterflow, vertical discharge, blow thru design, with fan assemblies built into pan and casing.

B. Provide [_____] liquid coolers having capacity to cool [_____] gpm of water from [_____] degrees F to [_____] degrees F with [_____] degrees F entering air WB temperature, and with pump circulating [_____] gpm with [_____] hp motor.  Design to operate against [_____] inch wg external static pressure with [_____] motors at [_____] hp.

2.03 COMPONENTS

A. Pan and Casing: Galvanized steel, [12 gage] [14 gage] for casing and 8 gage for reinforcing angles and channels with access doors at both ends of cooler to air plenum, lift out steel strainer, bleed line (from pump discharge) with valve [, inlet and outlet silencers] [, discharge hood with access doors ] [, duct flanges on inlet and outlet.]

B. Cooler Coil: Steel tubing, air tested under water to 350 psig, sloped to ensure drainage, encased in steel framework.  [Provide cleanable [header] [tube] unit with removable cover plates on header to access tubular coil.]

C. Fans: Multi blade, cast aluminum, axial type] [Forward curved centrifugal type mounted on steel shaft], with belt drive, bearings with ANSI/AFBMA life expectancy at 30,000 hours, with extended grease fittings.

D. Fan Motors: [Single] [Two] speed [(1800/900 rpm)] mounted on adjustable steel base.

E. V-Belt Drive: Cast iron or steel sheaves, dynamically balanced, keyed.  Variable and adjustable pitch sheave for motors 15 hp and under, selected so required rpm is obtained with sheaves set at mid-position.  Fixed sheave for 20 hp and over, matched belts.  Drive rated minimum 1.5 times nameplate rating of motor.

F. Fan Guard: Removable, welded steel rod and wire guard.

G. Distribution Section: [Polyvinyl chloride] [Galvanized steel] piping header and branches with [ABS] plastic spray nozzles.

H. Fill: Wave formed sheets of polyvinyl chloride plastic, self extinguishing with flame spread rating of [5] [10] to ASTM.

I. Drift Eliminators: Two or three pass formed steel, minimum 24 gage (0.6 mm), to limit drift loss to [0.7] [0.2] percent of total water circulated.

J. Float Valves: Brass or bronze [balanced piston type] make- up valve with plastic or copper float.

K. Hardware: Galvanized steel nuts, bolts, and washers stainless steel 0.25 inch nuts, bolts, washers, and nails.  [Assemble with phenolic epoxy coated, cadmium plated washer head fasteners.]

L. Finish of steel components:  hot dipped galvanized steel with zinc chromatized aluminum paint.

M. Pump: Close coupled, bronze fitted, centrifugal pump with mechanical seal, mounted on piping [controlled by pan mounted immersion thermostat set at [140 degrees F] [180 degrees F].]

N. Pump motor: [Single] [Two] speed [(1800/900 rpm)] open drip proof mounted on pump body.

2.04 ACCESSORIES

A. Electric Immersion Heaters: In pan suitable to maintain temperature of water in basin at 42 degrees F when outside temperature is 0 degrees F and wind velocity is 15 mph; immersion thermostat and float control to operate heaters on low temperature when pan is filled.

B. Electric Temperature Controller: In pan, set at [140 degrees F] [180 degrees F]; with sensor to cycle fans.

C. Time Delay Relay: Limits fan motor starts to not more than six per hour.

D. Capacity Control: Consists of scroll damper and modulating electronic damper motor controlled by temperature controller; sensor in pan set at [140 degrees F.] [180 degrees F.]

2.05 FACTORY FINISHING

A. Finish of steel componen:  hot dipped galvanized steel with zinc chromatized aluminum paint.

3.00 EXECUTION

3.01 EXAMINATION

A. Verify that openings are ready to receive work.

B. Verify field measurements are as shown on Drawings.

C. Verify that required utilities are available, in proper location, and ready to use.

D. Beginning of installation means installer accepts existing conditions.

3.02 INSTALLATION

A. Install in accordance with manufacturer's instructions.

B. Install cooler on structural steel beams as instructed by manufacturer.

C. Install cooler on vibration isolators.

D. Connect cooler water piping with flanged connections to cooler.

E. Connect make-up water piping with flanged or union connections to cooler.  Pitch to cooler.  Pipe drain, overflow drain, and bleed line to nearest floor drain.

3.03 INTERFACE WITH OTHER PRODUCTS

A. Ensure capacities are adequate for [Computer Room Air Conditioning Units.] [Packaged Engine Generator Set.]

3.04 ADJUSTING

A. Adjust water level float valves and float controls for proper operating level.

B. Adjust bleed valve for proportion of circulated water.

C. Adjust temperature controls and verify operation.

3.05 DEMONSTRATION

A. Provide systems demonstration under provisions of Section [01670.] [_____.]

B. Provide operation test to demonstrate operation in accordance with specified requirements.

END OF SECTION

G:\PUBLIC\MASTER\WRD97SPC\M\15730M.DOC
MASTER MECHANICAL
SECTION 15730 - 5
SPECIFICATION
LIQUID COOLERS


REV. 12/99


