C:\Ida's Folder\Spec Revisions\Mechanical Reformatted\15821M.DOC

SECTION 15821

SPRAYED COIL DEHUMIDIFIERS

1.00 GENERAL

1.01 PRINCIPAL WORK IN THIS SECTION

A. Sprayed coil dehumidifier units.

B. Spray pumps.

C. Insulation.

1.02 SUBMITTALS

A. Product Data:  Catalog cuts giving general assembly, dimensions, weights, materials, and certified performance ratings.

1.03 OPERATION AND MAINTENANCE DATA

A. Operation Data: Include assembly instructions, float adjustment, bleed rates, and electrical requirements.

B. Maintenance Data: Include instructions for lubrication filter replacement, cleaning and spare parts lists.

2.00 PRODUCTS

2.01 MANUFACTURERS

A. [___________________________________] Model [__________.]

B. [___________________________________] Model [__________.]

C. [___________________________________] Model [__________.]

2.02 MANUFACTURED UNITS

A. Units: Factory assembled consisting of casing, tank, spray headers, nozzles, [spray pumps,] water and drain connections, and cooling coils.

B. Evaporation Performance: [_____] cu ft/min with maximum air pressure drop [_____] inch wg, saturation efficiency minimum [_____] percent.

C. Operating Static Pressure: [3 inch wg negative.] [3 inch wg positive.] [6 inch wg positive.]

2.03 CASING

A. Assembly: Galvanized steel, minimum 16 gage (1.5 mm), reinforced and braced with galvanized steel angles with cadmium plated cap screws.

B. Connection: 1-1/2 inch flanges on inlet and outlet with 1/4 x 1 inch adhesive backed neoprene gasket.

C. Doors: [20 x 36 inch] [14 x 19 inch] quick opening access door on one side with 1/4 inch thick plexiglass inspection window.

D. Finish: Two coats of [zinc chromate, iron oxide, phenolic resin] [__________] paint applied after assembly.

E. Removable Inlet Screen: Galvanized expanded metal on inlet side of dehumidifier.

F. Gasket and flange pipe penetrations, inspection panels, access doors, and other openings in casing.

2.04 DRAIN TANK

A. Tank: Welded [black] [stainless] steel, 12 inches deep, [10 gage] [3/16 inch], [finished inside and out with zinc chromate, iron oxide, phenolic resin paint] [prime coated] and coated inside with [1/8 inch asphalt mastic] [3/32 inch epoxy] [glass fiber reinforced plastic] coating.

B. Connections: [3/4 inch] [1 inch] adjustable float valve assembly with brass rod and [brass] [polystyrene] float; [2 inch] [3 inch] [1- 1/2 inch] drain and overflow with removable copper suction screen.

C. Fabricate: Lap and weld corners watertight.  Weld fittings and piping supports to tank.

D. External Spray Piping: [1-1/4 inch galvanized steel] [1-1/2 inch PVC] piping.

E. Spray Nozzles: Bronze, self-cleaning.

2.05 COOLING COILS

A. Coil:  Refer to Section 15790.

B. Eliminators: [Galvanized steel,] [Type 304 stainless steel,] [PVC] mounted over drain pan.

2.06 SPRAY PUMPS

A. Type: [Vertical] [Horizontal] shaft, single stage, close coupled, radially split casing, for 125 psig maximum working pressure.

B. Casing: Cast iron, with gage ports, drain plug, flanged suction and discharge.

C. Impeller: Bronze, fully enclosed, keyed to motor shaft extension.

D. Shaft: Stainless steel.

E. Seal: Carbon rotating against a stationary ceramic seat.

F. Performance:

1. Flow Capacity: [_____] gpm.

2. Head: [_____].

3. Motor: [_____] hp.

4. Model: [__________] manufactured by [_______________].

3.00 EXECUTION

3.01 INSTALLATION

A. Install in accordance with manufacturer's instructions.

B. Install in ducts or casings in accordance with SMACNA HVAC Duct Construction Standards, Metal and Flexible.

C. Insulate exterior of unit same as specified for ductwork.

D. Place unit on 2 inch thick rigid insulation board same size as unit tank.  Flash and counterflash with 20 gage galvanized steel on entering and leaving sides.

E. Connect unit to water supply.  Provide gate valve on water supply line.  Provide 3/4 inch hose bibb accessible from interior.

F. Provide shut-off valves for individual spray header isolation and balancing.  [Arrange to permit step control of sprays.]

G. Pipe drain and overflow to nearest floor drain.

H. Bolt spray pump directly to tank fitting.  Insulate external spray piping.

I. Provide globe valve and solenoid valve in 1/2 inch bleed line from drain.

OR

J. Provide 1/2 inch bleed line from spray pump discharge to nearest floor drain complete with globe valve set to pass 1/2 gph per 1000 cu ft/min.  Locate bleed line above flood level of drain tank.

K. Provide low water cut-off in drain pan to stop spray pump.

L. Connect unit to [cold water cooling] [refrigerant] system.

M. Connect unit to electrical supply.

END OF SECTION

G:\PUBLIC\MASTER\WRD97SPC\M\15821M.DOC
MASTER MECHANICAL
SECTION 15821 - 3
SPECIFICATION
SPRAYED COIL DEHUMIDIFIERS


REV. 12/99


