http://www.syska.net/Specs/Mechanical/15870M-Power%20Ventilators.doc

SECTION 15870

POWER VENTILATORS

1.00 GENERAL

1.01 PRINCIPal WORK IN THIS SECTION

A. Roof exhausters.

B. Wall exhausters.

C. Cabinet [exhaust] fans.

D. Ceiling exhaust fans.

1.02 QUALITY ASSURANCE

A. Refer to Section 15010, General Provisions, Mechanical.

1.03 SUBMITTALS

A. Submit product data for the following items per the provisions of Division 1 and this Division’s General Provisions.

1. Product Data:  Manufacturer’s data giving construction information and dimensions.  Include fan curves with specified operating point clearly plotted, sound power levels at rated capacity, and electrical characteristics and connection requirements.

1.04 OPERATION AND MAINTENANCE DATA

A. Maintenance Data:  Include instructions for lubrication, motor and drive replacement, spare parts list, and wiring diagrams.

1.05 EXTRA MATERIALS

A. Provide [two] [____] sets of belts for each fan.

2.00 PRODUCTS

2.01 ROOF [EXHAUSTERS] [VENTILATORS]

A. Manufacturers:

1. Greenheck, Model [________].

2. [_____________________________] Model [________].

3. ACME, Model [________].

4. Cook, Model [________].

B. Product Requirements:

1. Performance Ratings: Conform to AMCA 210 [and bear the AMCA Certified Rating Seal.]

2. Sound Ratings: AMCA 301, tested to AMCA 300 [,and bear AMCA Certified Sound Rating Seal.]

3. Fabrication: Conform to AMCA 99.

4. UL Compliance: UL listed and labeled, designed, manufactured, and tested in accordance with UL 705.

NOTE:
EDIT FOR TYPES.  IF BOTH HOODED AND UPBLAST ARE USED, EDIT ACCORDINGLY.

C. Fan Unit:  V-belt or direct driven as indicated, with [spun aluminum] [galvanized steel with baked on enamel] [fiberglass reinforced plastic] [upblast spun aluminum with grease tray] housing; resilient mounted motor; 1/2 inch mesh, 16 gage aluminum birdscreen; square base to suit roof curb with continuous curb gaskets.

D. Roof Curb:  [8] [12] [16] [20] [24] [___] high [self flashing] of [galvanized steel] [aluminum] with continuously welded seams, [built in cant strips] [one inch (25 mm) insulation and curb bottom] [interior baffle with acoustic insulation, curb bottom] [ventilated double wall] [hinged curb adapter], and factory installed nailer strip.

E. Electrical Characteristics and Components

1. Electrical Characteristics:

a. As indicated on drawings.

2. Motor:  [Refer to Section 15170, MOTORS AND CONTROLLERS.]

3. Wiring Terminations:  Provide terminal lugs to match branch circuit conductor quantities, sizes, and materials indicated.  Enclose terminal lugs in terminal box sized to NFPA 70.

4. Disconnect Switch:  Factory wired, non-fusible, in housing for thermal overload protected motor [and wall mounted [multiple speed switch] [or] [solid state speed controller]].

NOTE:  ENGINEER TO COORDINATE SIZES ON DRAWINGS FOR MAXIMUM VELOCITY.

F. Backdraft Damper:  Gravity actuated, aluminum multiple blade construction, felt edged with nylon bearings.  Maximum velocity, 1200 FPM.

G. Sheaves:  Cast iron or steel, dynamically balanced, bored to fit shafts and keyed; variable and adjustable pitch motor sheave selected so required rpm is obtained with sheaves set at mid-position; fan shaft with self aligning pre-lubricated ball bearings.

2.02 WALL EXHAUSTERS

A. Manufacturers:

1. Greenheck, Model [________].

2. [_____________________________] Model [________].

3. Cook, Model [________].

4. ACME, Model [________].

5. Pace Model [_________].

B. Fan Unit:  V-belt or direct driven with spun aluminum housing; resiliently mounted motor; 1/2 inch mesh, 16 gage aluminum bird screen.

C. Electrical Characteristics and Components

1. Electrical Characteristics:

a. As indicated on drawings.

2. Motor:  [Refer to Section 15170, MOTORS AND CONTROLLERS.]

3. Wiring Terminations:  Provide terminal lugs to match branch circuit conductor quantities, sizes, and materials indicated.  Enclose terminal lugs in terminal box sized to NFPA 70.

4. Disconnect Switch:  Factory wired, non-fusible, in housing for thermal overload protected motor [and wall mounted [multiple speed switch] [or] [solid state speed controller]].

D. Backdraft Damper:  Gravity activated, aluminum multiple blade construction, felt edged with nylon bearings.

E. Sheaves:  For V-belt drives, provide cast iron or steel, dynamically balanced, bored to fit shafts and keyed; variable and adjustable pitch motor sheaves selected so required rpm is obtained with sheaves set at mid-position; fan shaft with self aligning pre-lubricated ball bearings.

2.03 CABINET AND CEILING EXHAUST FANS

A. Manufacturers:

1. Greenheck, Model [________].

2. [_____________________________] Model [________].

3. Cook, Model [________].

4. ACME, Model [________].

B. Centrifugal Fan Unit:  V-belt or direct driven with galvanized steel housing [lined with 1/2 inch (13 mm) acoustic insulation], resilient mounted motor, gravity backdraft damper in discharge.

C. Electrical Characteristics and Components:

1. Electrical Characteristics:

a. As indicated on drawings.

2. Motor:  [Refer to Section 15170.] 

3. Wiring Terminations:  Provide terminal lugs to match branch circuit conductor quantities, sizes, and materials indicated.  Enclose terminal lugs in terminal box sized to NFPA 70.

4. Disconnect Switch:  Cord and plug in housing for thermal overload protected motor [and wall mounted [switch] [multiple speed switch] [solid state speed controller]].

D. Grille:  Molded white plastic or aluminum with baked white enamel finish.

E. Sheaves: Cast iron or steel, dynamically balanced, bored to fit shafts and keyed; variable and adjustable pitch motor sheaves selected so required rpm is obtained with sheaves set at mid-position; fan shaft with self-aligning pre-lubricated ball bearings.

3.00 EXECUTION

3.01 INSTALLATION

A. Install in accordance with manufacturer's instructions.

B. Secure [roof] [wall] exhausters with [cadmium plated steel] [aluminum] [stainless steel] lag screws to [roof curb] [structure].

C. Extend ducts to [roof] [wall] exhausters into [roof curb] [structure].  Counterflash duct to [roof] [wall] opening.

D. Install flexible connections specified in Section 15910 between fan inlet and ductwork.  Ensure metal bands of connectors are parallel with minimum one inch flex between ductwork and fan while running.

E. Provide sheaves required for final air balance.

F. Install backdraft dampers on inlet to roof and wall exhausters.

G. Provide backdraft dampers on outlet from cabinet and ceiling exhauster fans and as indicated.

H. Do not operate fans for any purpose until project and ductwork are clean, filters in place, bearings lubricated, and fan has been test run under observation.

END OF SECTION

http://www.syska.net/Specs/Mechanical/15870M-Power%20Ventilators.doc
MASTER MECHANICAL
SECTION 15870 - 1
SPECIFICATION
POWER VENTILATORS


REV. 03/00


