G:\spec revision\M\15886M.NEW.doc

SECTION 15886

DUST COLLECTION SYSTEMS

1.00 GENERAL

1.01 PRINCIPAL WORK IN THIS SECTION Industrial exhaust fans.

A. Ductwork and duct fittings.

B. Inlet fittings.

C. Dust elimination and collection devices.

D. Accessories.

1.02 SUBMITTALS

A. Shop Drawings:   Indicate dimensions, sizes, weights and point loadings, material thickness, and locations and sizes of field connections.  [Submit construction layout and details for inlet fittings.]

B. Product Data:  Provide manufacturers literature and data indicating rated capacities, dimensions, weights and point loadings, accessories, electrical requirements and wiring diagrams, and location and sizes of field connections.

C. Provide fan curves with specified operating point clearly plotted.

D. Submit sound power levels for both fan inlet and outlet at rated capacity.

1.03 OPERATION AND MAINTENANCE DATA

A. Operation Data:   Include instructions for lubrication, motor and drive replacement, spare parts list, and wiring diagrams.

1.04 QUALITY ASSURANCE

A. Fans:

1. Performance Ratings: Conform to AMCA 210 [and bear the AMCA Certified Rating Seal.]

2. Sound Ratings: AMCA 301, tested to AMCA 300 [, and bear AMCA Certified Sound Rating Seal.]

3. Fabrication:  Conform to AMCA 99.

2.00 PRODUCTS

2.01 SYSTEMS MANUFACTURERS

A. [_____________________________].

B. [_____________________________].

C. [_____________________________].

2.02 CENTRIFUGAL FANS

A. Manufacturers:

1. [__________________________].

2. [__________________________].

3. [__________________________].

B. Base performance on [sea level] [_____________] conditions.

C. Wheel and inlet:

1. Backward Inclined: Steel construction with smooth curved inlet flange, heavy back plate, backwardly curved blades welded or riveted to flange and back plate; cast iron hub riveted to back plate and keyed to shaft with set screws.

2. Radial: Steel construction with [inlet flange,] heavy reinforced] back plate, plate blades [with reinforcing gussets] [and] [wearing strips] welded or riveted to back plate [and flange]; cast iron hub riveted to back plate and keyed to shaft with set screws.

D. Housing:  Heavy gauge steel, [spot welded] [continuously welded] with inlet bell and shaped cut‑off, factory finished with enamel or prime coat.  [Provide bolted construction with horizontal flanged split housing.]

E. Motors and Drives:

1. Motors:  As indicated, in compliance with Section 15170.

2. Bearings:  Heavy duty pillow block type, self aligning, grease lubricated ball bearings or roller bearings.

3. Shafts: Hot rolled steel, ground and polished, with key‑way, protectively coated with lubricating oil.

4. V‑Belt Drive:  Cast iron or steel sheaves, dynamically balanced, keyed; variable and adjustable pitch for motors 15 hp and under; fixed sheaves for motors 20 hp and over, matched belts, and rated minimum 1.5 times nameplate rating of motor.

5. Belt Guard: Fabricate to SMACNA HVAC Duct Construction Standards ‑ Metal and Flexible; of 12 gage, 3/4 inch diamond mesh wire screen welded to steel angle frame or equivalent, prime coated.

F. Accessories

1. Fixed Inlet Vanes: Steel construction with fixed cantilevered inlet guide vanes welded to inlet bell.

2. Adjustable Inlet Vanes: Steel construction with blades [supported at both ends] [cantilevered] with two permanently lubricated bearings, variable mechanism [out of air steam] terminating in single control lever with control shaft for double width fans and locking quadrant.]

3. Discharge Dampers: [Parallel] [Opposed] blade heavy duty steel damper assembly with blades constructed of two plates formed around and welded to shaft, channel frame, sealed ball bearings, with blades linked out of air stream to single control lever.

4. Inlet/Outlet Screens: Galvanized steel welded grid.

2.03 DUCTWORK AND DUCT ACCESSORIES

A. Materials:

1. Galvanized Steel Ducts:   ASTM A 525 or ASTM A 527 galvanized steel sheet, lock‑forming quality, having G90 zinc coating in conformance with ASTM A 90 [,minimum] [_____] gage ([_____]mm).

2. Steel Ducts: ASTM A 569 carbon steel [,minimum] [_____] gage ([_____]mm).

3. Stainless steel Ducts: ASTM A 167, Type [304] [____][,minimum] [_____] gage ([_____]mm).

4. Glass Fiber Reinforced Plastic Ducts:  NBS Voluntary Product Standard PS 15, UL 181, [‑__________].

B. Ductwork

1. Fabricate and support in accordance with SMACNA [HVAC Duct Construction Standards ‑ Metal and Flexible [2] [_____] pressure class [Round Industrial Duct Construction Standard and Rectangular Industrial Duct Construction Standard] and ACGIH Industrial Ventilation Manual except as indicated.

2. Construct T's, bends, and elbows with radius of not less than 11/2 times width of duct on centerline.

3. Increase duct sizes gradually, not exceeding 15 degrees divergence wherever possible.  Divergence upstream of equipment shall not exceed 30 degrees; convergence downstream shall not exceed 45 degrees. [, minimum] [_____] gage.

4. Fabricate continuously welded round and oval duct fittings two gauges heavier than duct gauges indicated in SMACNA Standard.  Prime coat welded joints.

5. Use crimp joints with or without bead for joining round duct sizes [8] [ ___] inch and smaller with crimp in direction of air flow, with liquid adhesive plus sheet metal screws.

6. Joints shall be minimum 4 inch cemented slip joint, brazed, or electric welded.

7. Provide standard 45 degree lateral wye branch fittings unless otherwise indicated.

8. Use double nuts and lock washers on threaded rod supports.

C. Flexible Connectors:  UL 214 listed, fire‑retardant chloroprene or chlorosulfonated polyethylene impregnated fabric, minimum density [20] [36] oz per sq yd ([0.68] [1.22] kg/sq m), approximately [2] [3] [6] inches ([50] [75] [150] mm) wide, crimped into metal edging strip.

D. Angle rings:  Carbon Steel, unpainted, leg out, drilled with bolt holes.

E. Blast Gates: [Half] [Full] collar of [cast aluminum] [steel], with galvanized steel slide, set screw.

F. Flat Back Elbows:  Long radius rectangular elbow at duct material with heavy gage, removable, [stainless steel] [rubber lined] [________] back strip.

G. Ball Joints:  [Cast iron] [Spun galvanized steel] with tubular studs for connecting ducts, allowing 25 degree angle off center.

2.04 INLET FITTINGS

A. Fabricate of  [minimum [16 gage [_____]] [galvanized] [carbon] [stainless] steel.

B. Fabricate inlet for [_________] to [detail indicated on Drawings] [ ACGIH Industrial Ventilation Manual detail print number] [_________] [indicated in Schedule].

C. Fabricate with hemmed edges, closed corners, and reinforced for span and attachment; with duct connection [;prime coated] [;enamelled finish].

2.05 FILTER SEPARATOR

A. Manufacturers:

1. [_______________________]

2. [_______________________].

3. [_______________________].

B. Indoor dust collector consisting of structural frame and casing, filters, fan and accessories.

C. Frame and Casing:  Steel frame with enamel finish, [16] [18] gauge galvanized steel panels, [_____] x [____] inch floor area, [____] cubic feet dust storage capacity [bin] [bags].

D. Filter: [Polyester] [______] fabric filters, [12] [____] ounces/sq yd density, [_____] square feet filter area, [99.9] [_____] percent dust spot efficiency.

E. Fan:  Welded construction centrifugal fan with material handling wheel, direct drive.

1. Capacity:  [_____] CFM at [____] inch WG static pressure.

2. Motor:
[_____]hp, [_____] volt, [single] [three] phase, 60 Hz.

F. Accessories:  [Manual shaker] [Powered shaker] [Differential static pressure gage] [Discharge silencer] [Push Button control panel with motor starter].

G. Model [_______] manufactured by [____________________].

2.06 CENTRIFUGAL SEPARATOR

A. Manufacturers:

1. [_______________________].

2. [_______________________].

3. [_______________________].

B. Cyclone dust collector consisting of cyclone with integral fan and structural stand incorporation dust storage.

C. Frame and Casing:  Steel frame with enamelled finish, [16] [_____] gage structure with [18] [_____] gage panels and [20] [_____] ([0.9][________] cyclone, [_______] cubic feet dust storage capacity.

D. Cyclone Efficiency: [99] [84] [_____] percent of [steel grindings] [sawdust] [baking flour] [corn starch] [_______________].

E. Fan:  Welded construction centrifugal fan with material handling wheel, direct drive.

1. Capacity:  [_____] CFM at [____] inch WG static pressure.

2. Motor:
[_____], [_____] volt, [single][three] phase, 60 Hz.

F. Accessories:  [Discharge silencer] [Push Button control panel with motor starter].Model [_______] manufactured by [____________________].

3.00 EXECUTION

3.01 INSTALLATION

A. Install equipment in accordance with manufacturers instructions.

B. Do not operate fans for any purpose until ductwork is clean, filters are in place, bearings lubricated, and fan has been test run under observation.

C. Install fans with resilient mountings and flexible electrical leads.  Refer to Section 15242.

D. Install flexible connections at [fan] [separator] inlet and discharge.  Ensure metal bands of connectors are parallel with minimum one inch (25 mm) flex between ductwork and fan while running.

E. Provide pitot tube openings where required for testing of systems, complete with metal cap with spring device or screw to ensure against air leakage.

F. Locate ducts with sufficient space around equipment to allow normal operating and maintenance activities.

END OF SECTION

G:\PUBLIC\MASTER\WRD97SPC\M\15886M.DOC
MASTER MECHANICAL
SECTION 15886 - 6
SPECIFICATION
DUST COLLECTION SYSTEMS


REV. 12/99


