http://www.syska.net/Specs/Mechanical/15890M-Ductwork.doc

SECTION 15890

DUCTWORK

1.00 GENERAL

1.01 PRINCIPAL WORK IN THIS SECTION

A. Provide labor, materials, and services necessary for a complete installation of the following:

1. Low pressure ducts.

2. Medium and high pressure ductwork.

3. Casings, plenums and equipment housing.

4. Buried ducts.

5. Wet exhaust ductwork.

6. Kitchen hood ductwork.

7. Fume hood exhaust ductwork.

8. Duct cleaning.

1.02 quality assurance

A. Refer to Section 15010, General Provisions, Mechanical.

B. Construct ductwork to [NFPA 90A] [and] [NFPA 90B] [and] [NFPA 96] standards.

NOTE:
90A INSTALLATION OF A/C AND VENTILATING SYSTEMS 90B WARM AIR HEATING AND AIR CONDITIONING SYSTEMS 96  INSTALLATION OF THE EQUIPMENT FOR REMOVAL OF SMOKE AND GREASE LADEN VAPORS FROM COMMERCIAL EQUIPMENT

C. Duct system shall be constructed, installed, sealed and insulated as provided in Chapter 6 of the [California] [Uniform] Mechanical Code.

1.03 SUBMITTALS

A. Submit product data, drawings, and schedules for the following items per the provisions of Division 1 and this Division’s General provisions.

NOTE:
THIS SHOULD BE A NUMERICAL LIST OF DETAILED ITEMS THAT THE ENGINEER WISHES TO REVIEW.  IT SHOULD BE SPECIFIC AND NOT VAGUE.  A DATABASE WILL BE GENERATED FROM THIS LIST (FOR EACH INDIVIDUAL PROJECT) AND THE SHOP DRAWING DEPARTMENT WILL TRACK THE PERFORMANCE OF THE CONTRACTOR.  THIS WILL TAKE THE GUESS-WORK OUT OF WHICH SUBMITTALS HAVE BEEN SUBMITTED AND WILL ALLOW US TO PRO-ACTIVELY KEEP THE CONSTRUCTION PROCESS ON SCHEDULE.

KEEP IN MIND THAT ANYTHING REQUESTED IN THE GENERAL PROVISIONS SECTION WILL BE TRACKED UNDER THE GENERAL DIVISIONS FILE (BY THE SHOP DRAWING DEPARTMENT). KEEP 1.03 SIMPLE AND ONLY HAVE A 1.03 A AND NO 103 B.

IF ITEMS ARE LENGTHY, PROVIDE A ONE OR TWO WORD DESCRIPTION WITH A COLON, FOLLOWED BY THE MORE LENGTHY DESCRIPTION.

1. Product data:  Manufacturer’s data on all factory made items specified herein.

2. Drawings:  Coordinated layout duct drawings that differ from ductwork shown on contract drawings.  Mechanical equipment room plans and sections showing all equipment, curbs, and accessories at minimum 3/8 in. scale, double line, showing sizes, transverse joints, transitions, elevations, clearances, accessories, and sections where required.  Show details of casing and plenum construction.

3. Schedules:  Ductwork construction, including gauge and bracing schedules.

1.04 DEFINITIONS

A. Duct Sizes:  Shown on the plans as clear inside dimensions.  For lined ducts, maintain sizes inside lining.

B. Seam:  locks or weld applied longitudinally to close section of duct, e.g. longitudinal seam, spiral seam.

C. Joint:  abutting connection between duct sections for continuity of air passage, e.g. cross joint, transverse joint, coupling.

D. Reinforcement:  hardware applied to strengthen duct, e.g. girth angles, tie rods, fasteners (not connectors), etc.

E. Stiffening:  folding, bending, beading, crossbreaking or corrugating of sheets to achieve strength through shape, e.g. pocket lock secures joint and is transverse stiffener, with girth angle and/or fasteners applied (not connectors), joint or stiffener is reinforced.

1.05 DUCT CLASSIFICATION

A. Velocity:

1. Low:  to 2000 ft. per minute.

2. Medium or high:  above 2000 ft. per minute.

B. Pressure:  

1. Based on following:

a. Single duct systems:  static pressure at respective point in ductwork during normal operation.

b. Variable volume systems:  from fan discharge to variable volume units, based on static pressure at beginning of fan discharge duct.

2. Pressure classification:  except as noted:

a. Low:  to 2 in. w.g.

b. Medium:  above 2 in. to 6 in. w.g.

c. High:  above 6 in. to 10 in. w.g.

C. System Schedule:

OPTION 1

1. High:  Supply from air handling units (or fans) to terminal boxes.

OPTION 2

2. Medium:  Supply from air handling units (or fans) to terminal boxes.

3. Low:

a. Supply:  terminal boxes to outlets.

b. Return.

c. Exhaust.

d. Transfer.

4. (Specify others).

1.06 DELIVERY, STORAGE, AND HANDLING

A. Deliver products to site under provisions of Division 1.

B. Store and protect products under provisions of Division 1.

2.00 PRODUCTS

2.01 BASE BID MANUFACTURERS

A. Flat oval and round duct and fittings:  

1. United Sheet Metal Division.

2. United McGill Corporation.

3. US Air Duct Corporation.

B. Flexible ducts (low pressure):  

1. General Environment Corporation.

2. H.K. Porter Co.

3. Wiremold Co.

4. Clevaflex Div.

5. Clevepak Corp. 

6. Flexaust Co.

C. Flexible Ducts (medium pressure):

1. Wiremold Co.

2. Automation Industries, Inc.: Thermaflex

3. United Sheet Metal Division, United McGill.

4. Clevepak Corp.

D. Duct Sealants:

1. Benjamin Foster Corp.

2. Minnesota Mining Manufacturing Co. (3M)

3. United Sheet Metal Division.

4. United McGill Corporation.

5. Miracle Adhesives, Corp. 

6. HardCast, Inc.

E. Double Wall Casings:  

1. Industrial Acoustics Co.

2. Keene Corporation.

3. Noise Control Division.

4. United Sheet Metal Division

5. United McGill Corp.

F. Underground Ducts:

1. Johns-Manville "Air-Duct".

2. United Sheet Metal Division Untied McGill.

G. Underground Tunnels:

1. Armco.

H. Metal Decking:

1. Robertson "Q-Deck".

2. Milcor "Celluflor".

I. Spring Fasteners

1. Dzus.

2. Simmons "Quick-Lock".

J. Duct Protective Coatings:

1. Wisconsin Protective Coating, Inc.

2. Varni-lite Corp. of America.

K. Spin-in Fittings:

1. Young & Co., Manufacturing.

2. Modular Metals.

L. Mechanical Duct Coupling Systems:

1. Ductmate Industries, Inc., or equal.

2.02 MATERIALS

A. Metal sheets shall be as follows:

1. Galvanized steel shall be in accordance with ASTM 5261; black or galvanized as herein after specified.

2. Stainless steel sheets shall be in accordance with AISI Types 302, 309 and 315.  Concealed ducts shall be finish No. 2B or No. 3.  Exposed ducts shall be finish No. 3 or No. 4.

3. Copper shall be in accordance with Federal Specification ZZ-C-567, light cold rolled (cornice) temper.

4. Stainless steel shall be in accordance with Federal Specification ZZ-S-766c, Class 3041.

5. Lead shall be in accordance with Federal Specification ZZ-L-301a, Grade C, 0.24 in. thick.

NOTE:
USE OF CEMENT ASBESTOS AND FIBROUS GLASS DUCT MATERIAL IS PROHIBITED.

2.03 DUCTWORK

A. Ductwork shall be galvanized steel, except as noted, in accordance with SMACNA HVAC Duct construction Standard, 1985, except as noted.  Provide gauges, construction and reinforcement as follows:

1. Pressure class 2 in. w.g.

a. Sheet metal gauge and reinforcement shall be in accordance with SMACNA Table 1-5 and 1-10 through 1-13 and based on a minimum of 2 in. w.g. duct pressure class regardless of possible lower pressures.  Round ductwork shall be spiral or longitudinal seam.  Cross breaking shall be as required for rigid support.

2. Pressure classes 2 in. w.g. to [6] [10] in. w.g.

a. Rectangular ductwork:  For pressure 2 in. w.g. to 6 in. w.g.  Sheet metal gauges and reinforcement in accordance with Pressure Class 6 in. w.g. -SMACNA- Table 1-8; based on 6 in. pressure, regardless of possible lower pressure.  [For pressure above 6 in. w.g. to 10 in. w.g. sheet metal gauges and requirements shall be in accordance with SMACNA - Table 1-9; based on 10 in. pressure, regardless of possible lower pressures.]  Ducts to 60 in. wide and within 30 ft. from fan discharge shall be next heavier listed gauge thickness to that indicated in SMACNA's Duct construction Standard.  Use Tables 1-10 through 1-13 for reinforcements.

1) Joints shall be welded flange, flanged joint and companion angle flanged joint only.  Inside slip (Fig. T9), double S slip (Fig. T8 and T80), standing seam (Fig. T-15 and T-16) and pocket lock (Figs. T17, T18 and T19) will not be permitted.  Fittings and/or joints of two different gauges, connected joint rating shall meet more stringent conditions.

b. Round ductwork shall be spiral seam construction only.  Gauges shall be in accordance with SMACNA Duct Construction Standard and fittings in accordance with SMACNA Duct Construction Standard, except as noted.

1) Joints:  Interior slip coupling beaded at center, fastened to duct with screws and with sealing compound applied continuously around joint before assembling and after fastening.  Wrap joints with 3 in. wide duct tape.

B. Watertight construction where noted with edges bent 1/2 in. for watertight seal.  Longitudinal seam sealant shall be 3M Brand No. 800; Alcoa, Aluminastic Type C, or solder; Stiffeners shall be plug or spot welded.  Transverse joints shall be bolted companion angles with 1/4 in. cadmium plated bolts with 6 in. minimum on centers and gasket.

NOTE:
COORDINATE THE USE OF MASONRY, CONCRETE ETC. AIR SHAFT WITH THE PROJECT MANAGER.  THE USE OF AIR SHAFTS OTHER THAN METAL MUST BE APPROVED.

C. Airtight construction where noted with longitudinal seams soldered.  Stiffeners shall be plug or spot welded.  Transverse joints shall be bolted companion angle with 1/4 in. cadmium plated bolts with 6 in. minimum or centers and gasket.  Exposed, uninsulated ductwork shall be flush flat seam.  Provide airtight concrete, masonry and other construction materials for plenums and shafts only where noted.

NOTE:
WHERE BUDGET DEMANDS LOWER COST WITH REASONABLE LONGEVITY OF MATERIAL, ALUMINIZED STEEL, TYPE 2 MAY BE THE CHOICE OVER PLAIN ALUMINUM, GALVANIZED STEEL AND STAINLESS STEEL.  THE MATERIAL HAS A LONGEVITY OF FOUR TO FIVE TIMES OVER GALVANIZED STEEL OF THE SAME GAUGE AND IS A GOOD SUBSTITUTE FOR STAINLESS STEEL ON HIGH PRESSURE SYSTEMS, WHERE ALUMINUM CANNOT BE USED, IN PRICE, IT STANDS BETWEEN ALUMINUM AND GALVANIZED STEEL.

SELECT MATERIAL FOR DUCTWORK INSTALLED WITHIN SHAFTS OPEN TO THE WEATHER AS IF EXPOSED TO WEATHER.

D. Ductwork exposed to weather, except as noted shall be as follows:

OPTION 1 AL1

1. Aluminum.

OPTION 2 AL1

2. Aluminized steel - Type 2.

OPTION 3 AL1

3. Copper.

OPTION 4 AL1

4. Stainless steel.

5. Watertight.

E. Outside air, exhaust and relief duct shall be as follows:

NOTE:
USE ONLY IN WET CLIMATES.

OPTION 1 AL2

1. Aluminum.

OPTION 2 AL2

2. Aluminized steel - Type 2.

OPTION 3 AL2

3. Copper.

OPTION 4 AL2

4. Stainless steel.

5. Extent:

NOTE:
LIST ANY EXCEPTIONS.

a. Within 10 ft. of louvers.

b. Louvers to casings.

c. Louvers to preheaters.

6. Watertight.

F. Shower exhaust duct for 15 ft. from registers shall be as follows:

1. Stainless steel.

2. Watertight.

G. Discharge duct from cooling towers shall be as follows:

1. Stainless steel.

2. Watertight.

H. Discharge duct from evaporative condensers shall be as follows:

1. Stainless steel.

2. Watertight.

I. Ductwork at duct humidifiers shall be as follows:

NOTE:
DO NOT SELECT ALUMINUM AT SPEAR HUMIDIFIERS.

OPTION 1 AL

1. Aluminum.

OPTION 2 AL

2. Aluminized steel - Type 2.

OPTION 3 AL

3. Copper.

OPTION 4  AL

4. Stainless steel.

5. Watertight.

6. Minimum 2 ft. upstream.

7. Minimum 10 ft. downstream.

NOTE:
CHECK LOCAL CODES ON USE OF PLASTIC MATERIALS; WHILE PLASTICS MAY NOT BE PERMITTED INSIDE BUILDINGS, THEY CAN BE USED OUTDOORS.  REVIEW WITH DEPARTMENT CHIEF ENGINEER.

J. Fume hood exhaust ductwork, provide as follows:

OPTION 1 EXHAUST

1. Stainless steel.

OPTION 2 EXHAUST

2. Fiberglass-reinforced polyester resins.

OPTION 3 EXHAUST

3. Plastic (resin or acid resistant material) coated steel.

OPTION 4 EXHAUST

4. Plastic (polyvinyl chloride).

OPTION 5 EXHAUST

5. Polyvinyl coated steel (PVC).

6. Welded or sealed watertight and airtight.

NOTE:
FOR HIGHLY CORROSIVE FUMES, PARTICULATES, OR MEDIUM AND HIGH PRESSURE SYSTEMS WHERE INDUSTRIAL QUALITY CONSTRUCTION IS DESIRED:  (REVIEW ACGIH MANUAL).

7. Construction shall be in accordance with ACGIH Industrial Ventilation Manual.

NOTE:
FOR EXHAUST DUCTWORK WITH HIGH PRESSURE.

8. Construction shall be in accordance with SMACNA rectangular industrial duct construction standards.

K. Canopy fume hoods shall be as follows:

1. ACGIH Industrial Ventilation Manual, unless noted otherwise.

NOTE:
CHECK LOCAL CODES FOR THICKNESS.

OPTION 1 TYPE

2. Furniture steel shall be No. 16 USSG, shop coat of prime lead base paint.

OPTION 2 TYPE

3. Stainless steel No. 16 USSG.

4. Internal angles and seams.

5. Bolts shall be countersunk.

6. Size, configuration and support shall be as indicated.

L. Water wash paint spray exhaust duct shall be as specified for watertight ductwork of respective pressure classification and pitch to:

OPTION 1 PITCH

1. Point of inlet.

OPTION 2 PITCH

2. Drain.

3. Provide drain flanges at low points and pipe to service sink or floor drain.  1 in. and smaller shall be copper, Type L.  1 1/2 in. and larger shall be galvanized steel.

M. Kitchen range hood exhaust duct including the discharge to atmosphere shall be provided as follows:

NOTE:
IF ALL DUCTWORK IS INSIDE BUILDING.

1. No. 16 manufacturer's standard gauge, black steel. 

NOTE:
CODE REQUIREMENTS ---- ALL DUCTWORK MUST BE WELDED AND THICKER BLACK STEEL IF SOME DUCTWORK IS OUTDOORS.  CHECK LOCAL CODE AREAS.

2. All seams, joints and penetrations shall be continuous liquid tight, welded, or brazed.

3. Angle reinforcing shall be minimum 1-1/2 in. x 1-1/2 in. x 3/16 in. at maximum 4 ft. on centers and in accordance with SMACNA Rectangular Industrial Duct Construction.

4. Cleanout doors on horizontal ducts shall be mounted maximum 20 ft. apart and at change of direction.  Cleanout doors on horizontal duct shall be mounted on side of duct.  Bottom edge shall be not less than 2 in. above bottom of duct.  Cleanout doors at vertical ducts shall be mounted at base.  Door and frame shall be same gauge as duct.  Gaskets shall be between door and frame.  Gaskets shall be 1/8 in. double thickness rated for 2000oF., Cleanout door size shall be maximum 24 in. x 24 in. and minimum shall be 24 in. one side, and other side shall be 2 in. less than duct height.

N. Wet exhaust duct from kitchen equipment or commercial dryer vent shall be as follows:

NOTE:
CHECK LOCAL CODE REGULATIONS FOR DUCT SYSTEM REQUIREMENTS AND MATERIAL FOR DUCTWORK.

OPTION 1 AL

1. Aluminum.

OPTION 2 AL

2. Aluminized steel - Type 2.

OPTION 3 AL

3. Stainless steel.

OPTION 4 AL

4. Copper.

5. Watertight.

O. Dishwasher exhaust duct shall be as follows:

NOTE:
CHECK LOCAL CODE REGULATIONS FOR DUCT SYSTEM REQUIREMENTS AND MATERIAL FOR DUCTWORK.

OPTION 1 DISHW

1. Stainless steel.

OPTION 2 DISHW

2. Aluminum and stainless steel from dishwasher to ceiling.

3. Watertight.

P. Paint spray booth (water wash type) exhaust duct shall be as follows:

OPTION 1 SPRAY

1. Galvanized steel.

OPTION 2 SPRAY

2. Aluminum.

3. Soldered watertight.

4. Construction in accordance with ACGIH Industrial Ventilation Manual.

Q. Swimming pool supply and exhaust, provide as follows:

OPTION 1 POOL

1. Aluminum.

OPTION 2 POOL

2. Stainless steel.

R. Underground ductwork, provide as follows:

OPTION 1 UNDER

1. Galvanized steel, factory coated with PVC - 0.004 in. outside, United Sheet Metal Uni-Coat or equal.

OPTION 2 UNDER

2. Galvanized steel, concrete encased.

OPTION 3 UNDER

3. Concrete pipe.

S. X-Ray Rooms ductwork or as noted shall be lead shielded.

2.04 FLEXIBLE DUCTS

A. General:

1. Use only where specified or indicated.

2. UL 181, Class I Air Duct.

3. Labeled for compliance with UMC.

B. Low Pressure:

1. Insulated Flexible Duct:

a. Minimum working pressure 2 in. w.g. positive and 1.5 in. w.g. negative.

b. Nominal 1 in. insulation with vapor barrier.

c. Maximum thermal conductivity 0.27 BTUH/sq. ft. degrees F/in at 75ºF.

2. Use at following locations:

a. Connection to ceiling supply air outlets.

b. As indicated.

3. Wiremold Type WG or equal.

C. Medium and High Pressure:

1. Insulated Flexible Duct:

a. Minimum working pressure 10 in. w.g.

b. Nominal 1-1/2 in. insulation.

c. Maximum thermal conductivity of 0.27 BTUH/sq. ft. degree F/in at 75ºF, with vapor barrier.

2. Use at following locations:

a. Inlet connections to terminal units.

b. Size to match terminal unit.

3. Wiremold type WK or equal.

NOTE:
NYC SHEET METAL CONTRACT LIMITS LENGTH OF FLEXIBLE DUCT, CHECK CAREFULLY WITH BUILDING CODE FOR ALLOWABLE SMOKE AND FLAME SPREAD RATINGS.

D. Flexible duct shall be constructed in accordance with NFPA 90A; U.L. 181 Class 1 (maximum flame spread:  25, maximum smoke developed:  50).  Performance and installation shall be in accordance with SMACNA HVAC Duct Construction Standards, Metal and Flexible.  Maximum length shall be [18 in.] with no intermediate seams.

NOTE:
FOR ECONOMY PROJECTS.

OPTION 1 FLEX

E. Flexible duct for class 2 in. w.g. shall be polyester reinforced aluminum foil over corrosion resistant wire helix, Wiremold WC or equal.

NOTE:
FOR QUALITY PROJECTS

OPTION 2 FLEX

F. Flexible duct for pressure class 2 in. w.g. shall be high temperature copolymer impregnated glass fabric, locked to cold rolled flat steel spiral, Wiremold 57 or equal.

NOTE:
INSTALL MAXIMUM PRESSURE.

OPTION 1 FLEX

G. Flexible duct for pressure classes 6 in w.g. to ------ in. w.g. shall be high temperature copolymer impregnated glass fabric, locked to cold rolled flat steel spiral,  Wiremold 57 or equal.

NOTE:
FOR HIGH QUALITY PROJECTS.  REVIEW COST BEFORE SPECIFYING.  INSTALL MAXIMUM PRESSURE.

OPTION 2 FLEX

H. Flexible duct for pressure classes 6 in w.g. to ----- in. w.g. shall be corrugated aluminum construction, bendable, self-supporting and mechanically interlocked to be totally leak proof under operating conditions without use of adhesives, Clevaflex Type 12 or equal.

NOTE:
FOR CONNECTION TO DIFFUSERS IN OPERATING ROOMS.

I. Flexible duct connections to oval collars shall be with preshaped oval ends.  Secure flexible duct with clamps and sealer or screws, sealer and tape for metal flexible ducting.  Attach to rectangular supply air duct with low entrance loss, bellmouth type connector on air inlet end.  Flexible shall not lay across lighting fixtures or other surfaces; provide hanger supports as required.

2.05 CASINGS, HOUSINGS AND PLENUMS

A. Pressure class 2 in. w.g. shall be galvanized steel unless otherwise noted:

OPTION 1 WALL

1. Single wall, minimum No. 16 USSG.

OPTION 2 WALL

2. Double wall, with insulation core.  Outer panel, minimum No. 18 USSG.  Inner panel, minimum No. 22 USSG and:

OPTION 1 SOLID

a. Solid.

NOTE:
WHEN SOUND ATTENUATION IS REQUIRED, REVIEW WITH DEPARTMENT CHIEF ENGINEER.

OPTION 2 SOLID

b. Perforated, except solid for cooling coil section to downstream of coil pans.

c. Core shall be 2 in. thick, fiberglass or rock mineral wool, 2-1/2 lb. minimum density.

NOTE:
APPLICABLE IF PERFORATED PANELS ARE SPECIFIED.

d. Refer to section Noise Control.  Plenums shall be Industrial Acoustics Quiet-Flow Plenum or approved equal.

3. Provide same construction for floor and ceiling of casing.

4. Provide for outdoor air intake plenums, exhaust plenums open to weather, and blow through units from fan discharge to leaving side of coil, as follows:

OPTION 1 TYPE

a. Aluminum; single wall, watertight.

OPTION 2 TYPE

b. Stainless steel; single wall, watertight.

NOTE:
INSERT MAXIMUM PRESSURE.

B. Pressure Classes 6 in. w.g. to ------ w.g. materials and wall shall be as specified for pressure Class 2 in. w.g.  For galvanized steel cellular deck, provide flat sheet on one side and where insulated, insulation shall be applied to flat side.  Casings shall be as follows:

NOTE:
INSERT MAXIMUM PRESSURE.

1. Pressure classes 3 in. w.g. to ------ in. w.g.

a. ---------.

b. ---------.

2.06 SOUNDLINED DUCTWORK

A. Refer to Section "Sound Attenuators."

B. Duct dimensions noted on drawings are clear inside dimensions.

2.07 ELIMINATORS

A. Eliminators shall be constructed, as follows:

NOTE:
ELIMINATORS SHOULD BE SHOWN ON DRAWINGS FOR SYSTEMS WHERE REQUIRED.

OPTION 1 GAUGE

1. No. 24 USSG stainless steel.

OPTION 2 GAUGE

2. No. 24 USSG galvanized steel.

OPTION 3 GAUGE

3. No. 24 USSG aluminized steel - Type 2.

OPTION 4 GAUGE

4. No. 24 B&S gauge aluminum.

5. Eliminators shall be in accordance with SMACNA Duct Construction Standards except as noted with 3 bends, 3 hooks and 45º deflection.  Nominal 6-1/2 in. front to back and maximum 2 in. apart.  Eliminators shall be removable.  Provide separate sections vertically to match coil banks and provide top, bottom and intermediate supports.  Locate over rear end of drain pan.  Provide eliminators as noted.

2.08 AUTOMATIC DAMPERS

A. Install automatic dampers supplied by automatic control system manufacturer.  Notch end of rod and label duct or casing to indicate open and closed position.

2.09 GLASS INSPECTION PANELS

A. Glass Inspection Panel where noted in access doors at electric coils in air handling units shall be 12 in. x 12 in. panel, except as noted.  Panels shall be wireglass gasketed and watertight.

2.010 FLEXIBLE CONNECTIONS

A. Flexible connections for ductwork shall be in accordance with SMACNA HVAC Duct Construction Standards, Metal and Flexible, except as noted.  Flexible connections with metal collars shall be installed with 2 in. slack in fabric and minimum movement of 1 in.  Provide flexible at connections to fans, building expansion joints, at connection between copper and stainless steel ductwork and at penetrations of mechanical equipment room walls.

1. Provide neoprene coated glass fabric, 30 oz. per sq. yd. with sewn and cemented seams, Vent Fabrics, Inc. or equal.  For kitchen exhaust, provide wire imbedded glass cloth with sewn seams as manufactured by Vent Fabrics.

2.011 TURNING VANES

A. For galvanized steel ductwork, provide galvanized steel [or painted black steel], except as noted.  For other ductwork, provide same material as ductwork.  Turning vanes shall be single thickness with flat trailing age, in accordance with SMACNA HVAC Duct Construction Standards, except as noted.

1. Install at square duct elbows and as noted on drawings.  Maximum unsupported vane length shall not exceed 48 in.  Provide separate equal size sections for greater lengths.  Refer to turning vane detail.  ASHRAE and SMACNA show better performance for single thickness.

B. Angles, tie rods and shapes for reinforcing joints shall be in accordance with SMACNA HVAC Duct Construction Standards, except for the following:

1. Reinforcing angle spacing shall not exceed 24 in. spacing and applied to four sides for following distances from fan inlet and outlet for each system.

a. Ten ft. for fans with wheel diameter to 27 in.

b. Twenty ft. for fans with wheel diameters exceeding 27 in.

2. Galvanized and aluminum sheets:  Provide galvanized steel.

3. Stainless steel sheets:  Provide stainless steel.

4. Copper sheets:  Provide stainless steel, brass or bronze.

C. Screws and rivets:  Provide the same material as sheet, except as noted.  On aluminum sheets, provide cadmium plated or stainless steel.  Zinc or cadmium plated will be permitted on galvanized sheets.  Minimum screw size shall be No. 10; maximums pacing shall be 10 in.  Minimum rivet size shall be 4 lb.; maximum spacing shall be 6 in.

D. Duct sealants:

1. Provide sealing compound for brush applications, 3M Brand No. 800 or equal and other applications, 3M Brand No. 900 or equal.  Provide tape, 3M No. 474 or equal.  For gaskets, provide continuous, reinforced, inert self-conforming type, 1/8 in. thick and width to match angle connection, 3M Weatherban 1202-T ribbon sealer or equal.

E. Refer to Installation for supports, hangers, inserts and attachments and the following special construction:

1. Stainless steel ductwork.

2. Aluminized steel - Type 2 ductwork.

3. Copper ductwork.

4. Spiral seam round or flat oval ductwork.

5. Lead shielding for ductwork.

3.00 EXECUTION

3.01 DUCTWORK INSTALLATION

A. General:

1. Construct with gauges, joints, bracing, reinforcing, and other details per latest UMC (or CMC), ASHRAE, SMACNA, (or NFPA) unless specified otherwise.

a. Comply with most stringent.

b. Provide ducts with NFPA 90A gauges when traversing smoke zones.

2. Construct of galvanized sheet metal, except where otherwise indicated.

3. Diagonally crossbreak all panels on metal rectangular ducts over 18 in. in either direction.

a. Beading for reinforcing not acceptable.

b. Crossbreak outward in ducts having positive internal pressure.

c. Crossbreak inward in ducts having negative internal pressure.

4. Duct dimensions indicated are net, inside, clear, dimensions.

a. For internally lined ducts, add lining thickness to determine metal duct dimensions.

5. Classification:  Classify and construct ducts per latest regulation as follows:

OPTION 2 

	
	LP
	LP
	LP
	MP
	MP
	MP
	HP

	SMACNA:
	½
	1
	2
	3
	4
	
	10

	SP in.:
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


6. Alter duct sizes on basis of equal friction where required to facilitate installation.

7. Avoid penetrations of ducts.

a. Provide airtight rubber grommets at unavoidable penetrations of hanger rods.

8. At exposed duct penetrations of walls, floors and ceilings, provide sheet metal angle type escutcheons.

9. At supply diffusers, grilles and/or registers extend branch duct 1 foot beyond air outlet, except as detailed otherwise.

10. Install exposed ducts to maintain not less than 7 ft. head clearance, unless indicated otherwise.

11. Tapers:

a. Pitch sides of duct in "diverging" or "converging" airflow maximum of 1 to 4 taper.

12. Duct openings:

a. Provide openings where required to accommodate thermometers smoke detectors, controllers, etc.

1) Insert through airtight rubber grommets.

b. Provide pitot tube openings where required for testing of systems:

1) Complete with metal cap with spring device or screw to ensure against air leakage.

2) For Pitot tube tests install Ventlok No. 699 and/or 699-2 instrument test holes.

c. Where openings are provided in insulated ductwork, install insulation material inside metal ring.

d. At fire dampers allow adequate length of duct to install access door.

13. Duct lining:

a. Install lining in ducts and plenums as specified in Section 15290:  DUCT INSULATION.

14. Flexible Duct Connections:

a. Coated glass fabric.

1) For indoor or outdoor use as specified hereinbefore.

b. Install at:

1) Connections to fans and air handling units.

2) In high velocity ducts at penetrations of mechanical equipment room walls.

a) As specified for fans.

3) Additional as indicated on drawings.

c. Install at building joints.

1) Seismic and/or expansion joints.

2) Minimum free motion required:

a) Axial:  ________ inches.

b) Transverse:  _______ inches.

15. Volume dampers.

a. See Section 15910, DUCT ACCESSORIES.

b. Install damper in every branch.

c. On branches with only one air outlet volume damper in outlet may be omitted.

B. Elbows and Transitions:

1. Construct radius elbows with inside radius not less than duct width.

2. Use square turns in rectangular ductwork, unless indicated otherwise, at following locations:

a. Exposed elbows.

b. Immediately upstream from supply air outlets.

c. Where required to facilitate installation.

3. Provide turning vanes in miter elbows in round and rectangular ducts.

4. Where indicated, provide elbow with splitter vanes of special size and shape, per SMACNA Duct Standards, Section 5.

5. In high and medium pressure ductwork spot weld turning vane to duct.

6. Two-way splits:

a. Supply, return and exhaust.

b. Two elbows:

1) Proportionally sized per SMACNA Duct Standards.

2) Radius or square.

c. Single fitting acceptable.

1) With turning vanes.

2) Duct openings sized as above.

C. Rectangular Duct Joints:

1. Standing seams, except where flush drive slip seam called for.

2. Use flush, drive-slip, for:

a. Exposed ducts:

1) Except in garages, mechanical rooms.

b. Where required for clearance.

3. "Ductmate" system joints, may be used in lieu of standing seams.

a. In ducts no wider than 60 in.

D. Joint Sealing:

1. Seal transverse and longitudinal joints of sheet metal ducts by one of following methods:

a. Six ounce canvas strip, six in. wide.

1) Adhere with lagging adhesive.

b. Hardcast PS-S tape.

c. United Hi-Velocity sealer.

d. Applications as recommended by manufacturer.

2. Seal punched holes and corner cracks.

3. After installation and testing reseal joints found to be leaking.

E. Ducts Out-of-Doors:

1. Make ducts water tight when subject to rain.

2. Construct as follows to assure water run-off:

a. Arrange standing seams to not act as dams.

b. Longitudinal seams at bottom of duct.

c. Slope entire top of duct down toward side.

d. Vertical struts within duct to bow top panels of duct into convex shape.

e. Mastic within sheet metal joints.

F. Special Materials and Construction:

NOTE:
FOR EXPOSED DUCTWORK IN FINISHED AREAS WHERE APPEARANCE IS IMPORTANT, CHECK WITH ARCHITECT AND DEPARTMENT CHIEF ENGINEER BEFORE USING.

1. Flush flat seam ductwork:  Provide for all exposed uninsulated ducts and transverse joint detail shall be as indicated.  Provide sheet metal 2 gauge numbers heavier than required for pressure classification with normal (standing) seam construction.  Provide all joints and seams, smooth and aligned with no projections.  For internal reinforcing, at transverse joints and on 2 ft. center, provide on ducts midpoint, on ducts 61 in. to 90 in. wide, provide 2 vertical stays at duct third (1/3) points and for ducts over 90 in. wide provide 3 vertical stays at ducts quarter (1/4) points.  For vertical stays:  provide 10 USSG galvanized steel, free of burrs and rough edges with both ends bent and fastened to top and bottom of duct.

NOTE:
WHERE RECOMMENDED FOR NOISE ABATEMENT BY ACOUSTICAL CONSULTANT.

2. Double wall rectangular ductwork:  for all ductwork in fan rooms, except exhaust and relief air ducts, provide ductwork made up of insulated panels, as follows:

a. Outside sheet shall be the same gauge as single wall ductwork.  Inside sheet shall be 2 gauge numbers lighter than outside sheet.  Sections over 24 in. long:  provide internally braced with Z-bars, pip riveted, 6 in. on centers to inside and outside sheets.  Panels shall be assembled with slide locks.  Seams shall be brazed at corners and spot brazed on 12 in. centers.

b. Transverse joint connections:  Provide continuous 1/8 in. thick neoprene gaskets, full thickness of insulated panel and between butted sections of ducts.  Covering strips, shall be No. 18 USSG, 2-1/2 in. wide strips completely around ducts, covering transverse joints and with edges lightly broken for stiffening.  Strips shall be fastened to duct with sheet metal screws, 8 in. on centers.  Screws shall penetrate outer sheet of panels only.

c. Solder shall be 50-50 hard bar type.  Caulking shall be #M "weatherban" or equal (polysulphide rubber, thiokal base, caulking compound).  Gaskets shall be 3M EC-1202 or equal.

3. Stainless steel ductwork:  Provide the following as specified for respective pressure classification:

a. Sheet metal gauge, except minimum No. 17 USSG where welded.  Where watertight is noted, joints and seams may be brazed with Eutectic Eutectrod No. 157 low temperature alloy wire.

b. Joints, seams and stiffening.

c. For stiffening angles, rivets and hardware, provide stainless steel.  Provide welded or brazed watertight joints and seams in sections where moisture may collect with welding or brazing ground smooth and pitch ductwork and provide drains as specified herein for watertight ductwork.  Provide connections between stainless steel and other materials made with insulating fabric gaskets.  Exposed ductwork in finished spaces shall be polished to match finish of equipment.

4. Aluminized steel - Type 2 ductwork:  Provide sheet metal gauge and joints, seams and stiffening as specified for respective pressure classification:

a. Stiffening angles:  For ductwork exposed to weather, provide galvanized steel, riveted or bolted with gasket separator under angles.  Paint cut edges with Rustoleum primer and final costs.

b. Provide cadmium plated steel or stainless steel rivets, bolts and hardware.  Make watertight joints and seams in sections where moisture may collect, and pitch ductwork and provide drains as specified herein for watertight ductwork.  Where ductwork is exposed to weather, apply sealing compound to all joints and seams.

5. Copper ductwork:  Provide joints, seams and stiffening as specified for galvanized steel ductwork, except stiffening angles shall be brass or steel with lead separators full area of angle between ductwork and stiffeners.

a. Weights:

1) To 30 in. wide:  20 oz.

2) 31 in. to 36 in. wide:  24 oz.

3) 37 in. to 48 in. wide:  26 oz.

4) 49 in. to 72 in. wide:  28 oz.

b. Provide copper rivets and hardware.  Provide watertight solder joints and seams in sections where moisture may collect and pitch ductwork and provide drains as specified herein for watertight ductwork.  Make connections between copper and steel work with insulation rubber fabric gaskets.

6. Aluminum ductwork:  Provide as specified for respective pressure classification and in accordance with SMACNA recommendations on aluminum duct, except as noted.  Construction shall be of equivalent Brown & Sharpe (B&S) gauges.  Seal all seams watertight.  Separate aluminum ducts, casings, plenums, housings and louvers from direct contact with concrete by resilient gasketing or caulking compound.

NOTE:
REVIEW WITH CHIEF MECHANICAL ENGINEER BEFORE INCLUDING THIS ARTICLE.  SPIRAL SEAM FLAT OVAL DUCTWORK IS MANUFACTURED FROM SPIRAL SEAM ROUND DUCTWORK.  SEE UNITED SHEET METAL CO., BULLETIN NO. FO7 FOR ECONOMICAL SIZES.  DUE TO MACHINE LIMITATIONS, WIDTHS UNDER 21 IN. NOT YET AVAILABLE.  12 FT. LENGTHS AVAILABLE.  DO NOT USE FOR PRESSURE CLASS UP TO 2 IN. W.G..  POSITIVE PRESSURE ONLY, NOT SUITABLE FOR NEGATIVE PRESSURES.  THIS ARTICLE SUITABLE FOR PRESSURE CLASSES 2 IN. W.G. TO 10 IN W.G.

7. Spiral seam flat oval ductwork:  for ductwork, provide spiral seam construction, galvanized steel of gauges as recommended by SMACNA HVAC Duct Construction Standards, except as noted.  For joints, provide interior slip coupling beaded at center, fastened to duct with screws and with sealing compound applied continuously around joint before assembly and after fastening.  Wrap joints with 3 in. wide duct tape.  Provide stiffening with full width reinforcement of both flat, major axis surfaces.  Stiffeners on both flat surfaces extending beyond major axis shall be secured with threaded rods.

a. For pressure class 2 in. w.g. stiffening shall be as follows:

1) Up to 26 in. wide:  none.

2) 27 in. to 34 in.:  1 in. x 1 in. x 1/8 in. angle, maximum 6 ft. centers.

3) 35 in. to 52 in. wide:  1-1/2 in. x 1-1/2 in. x 3/16 in. angles, maximum 6 ft. centers.

4) 53 in. to 60 in. wide:  1-1/2 in. x 1-1/2 in. x 3/16 in. angle, maximum 4 ft. centers.

5) 61 in. wide and larger:  2 in. x 2 in. x 3/16 in. angle, maximum 2 ft. centers.

b. For pressure class 3 in. to 6 in. w.g. stiffening shall be as follows:

1) Up to 34 in. wide:  1-1/2 in. x 1-1/2 in. x 1/8 in. angle, maximum 6 ft. centers.

2) 35 in. to 40 in.  wide:  1-1/2 in. x 1-1/2 in. x 3/16 in. angle, maximum 6 ft. centers.

3) 41 in. to 45 in. wide:  2 in. x 2 in. x 3/16 in. angle, maximum 6 ft. centers.

4) 46 in. to 60 in. wide:  2 in. x 2 in. x 3/16 in. angle, maximum 4 ft. centers.

5) 61 in. wide and larger:  2 in. x 2 in. x 3/16 in. angle, maximum 2 ft. centers.

c. For pressure class 10 in. w.g. stiffening shall be as follows:

1) Up to 26 in. wide:  1-1/2 in. x 1-1/2 in. x 1/8 in. angle, maximum 6 ft. centers.

2) 27 in. to 40 in. wide:  1-1/2 in. x 1-1/2 in. x 3/16 in. angle, maximum 6 ft. centers.

3) 41 in. to 52 in. wide:  2 in. x 2 in. x 3/16 in. angle, maximum 4 ft. centers.

4) 53 in. wide and larger:  2-1/2 in. x 2-1/2 in. x 3/16 in., maximum 2 ft. centers.

d. Within 30 ft. of fan:  Provide stiffeners of sizes specified, maximum 2 ft. centers.

1) Provide fittings in accordance with SMACNA HVAC Duct Construction Standards, except as noted.  Fittings shall be continuous weld, beaded end connections designed for flat oval ductwork.  Provide radius type elbows with centerline radius 1½ times duct width.  For branch connections, provide lateral, conical tees,  United Sheet Metal Co., Inc. or equal.

NOTE:
CHECK FOR ANY OTHER SPECIAL AREAS.

8. Lead shielded ductwork:  Provide lead shielded ductwork in and around x-ray room, as noted.  Sheet lead in contact with concrete, mortar or plaster shall have surfaces coated with heavy bituminous or latex material.  Joints shall be lapped minimum of 1 in. and soldered to form complete continuous seal.  Provide shielding construction, materials and equipment in conformance with applicable requirements of National Bureau of Standard, Handbook 60, Medical X-Ray Protection.  Shielding shall be installed in such manner that X-ray absorption at any point is not less than above requirements or adjacent lead protection.  Lead lining shall be securely installed, free of waves, lumps or wrinkles and with as few joints as possible.

3.02 DUCT HANGERS AND SUPPORTS

A. General:

1. Support horizontal ducts with hangers of size and spacing as indicated in pertinent SMACNA Duct Construction Standards.

2. Attachment to structure:  As specified in Section 15090:  SUPPORTS AND ANCHORS.

3. Vibration isolation for ducts:  As specified in Section 15242:  VIBRATION ISOLATION.

B. Horizontal Duct Supports:

1. Install hangers at each change in direction of duct.

2. Strap hangers:

a. Extend strap down both sides of ducts.

b. Turn under bottom 1 in. minimum.

c. Metal screw hangers to:

1) Bottom of duct.

2) Upper and lower sides of ducts.

3) Not more than 12 in. on center.

3. Angle hangers:

a. Provide angle hangers formed by extended vertical bracing angles.

b. Or by rods connecting to bottom angles if size or bracing angles conform to hanger schedule.

4. Vertical duct supports:

a. Support vertical ducts at every floor:

1) Use angles or channels riveted to ducts.

2) Set angles or channels on floor slab or structural steel members placed in opening, unless otherwise noted.

3.03 FIELD QUALITY CONTROL

COORDINATE WITH SECTIONS 15990, 15994.  SELECT AABC OR NEBB.

A. Testing, adjusting and balancing (TAB) shall be performed by an approved independent TAB Contractor.  Contractor qualification shall be Associated Air Balance Council (AABC) membership or National Environmental Balancing Bureau (NEBB) certification.  Qualifications of the firm, persons responsible for supervising and performing the work, and the Registered Professional Engineer who will certify the report, shall be submitted for approval.  Refer to Section 15990, TESTING, ADJUSTING, AND BALANCING OF HVAC SYSTEMS.

B. Procedure shall be in accordance with the AABC National Standards for Total System Balance.  Work shall include, but not be limited to the following:

1. Balance and adjustment of air distribution systems.

2. Test of systems to certify compliance with requirements of authorities having jurisdiction for ventilation and proper functioning of operating devices.

C. Before testing, examine air handling systems:  For filters, provide clean filters, free of air bypass and functioning as specified.  Lubricate moving equipment.

D. Other inspection and maintenance items for proper system operation:

1. Air handling equipment:  Demonstrate equipment performs as noted.  Adjust, variable type pulleys, variable inlet vanes and volume and control dampers.  Replace fixed pitch pulleys as required to balance systems.  Pulleys shall be supplied as specified in Section Air Handling System Equipment.

2. Air distribution:  Adjust dampers and registers to deliver or remove indicated air quantities for registers, diffusers and terminal units within plus or minus 10% in proper pattern so that there are no drafts.  Take Pitot readings in main trunk ducts in conjunction with inlet and outlet readings.

E. Leakage testing shall be in accordance with AABC National Standards.

F. Test reports:  Submit six (6) copies in bound folders with accompanying sketches.

1. Report forms shall be:

AABC OR NEBB

a. SMACNA, AABC or NEBB type.

b. Apparatus test reports.

c. Outlet test reports.

2. Additional report information:  Submit method of balancing and details of instruments used, including serial numbers and last date of calibration.  Submit copies of air velocity and pressure readings with duct layout showing where readings were taken.  Submit minimum and maximum air flow readings as measured for:

a. Outside air.

b. Return air.

c. Relief air.

d. Exhaust air.

e. Each terminal unit.

3. Submit Pitot readings.

G. Certification:  Report shall be certified by an independent Registered Professional Engineer not affiliated with construction phase of the project.  Certification shall include checking of air measurement calculations, factors, and procedures.

END OF SECTIOn

http://www.syska.net/Specs/Mechanical/15890M-Ductwork.doc
MASTER MECHANICAL
SECTION 15890 - 1
SPECIFICATION
DUCTWORK


REV. 03/00


