\\LAO-ENG-01\DATA\spec revision\M\15941m.new.doc

SECTION 15941

INTAKE AND RELIEF VENTILATORS

1.00 GENERAL

1.01 PRINCIPAL WORK IN THIS SECTION

A. Louvered penthouses.

B. Roof hoods.

1.02 QUALITY ASSURANCE

A. Refer to Section 15010, General Provisions, Mechanical.

1.03 SUBMITTALS

A. Submit product data and schedules for the following items per the provisions of Division 1 and this Division’s General Provisions.

1. Product data:  Manufacturer’s complete description including pictures, finishes, and complete performance data showing pressure drops.

2. Schedules:  Schedules of outlets and inlets clearly defining size, type, finish, and mounting for each.

2.00 PRODUCTS

2.01 louvered penthouses

A. Provide [4] [6] inch deep louvers with blades on 45 degree slope [with center baffle and return bend], heavy channel frame, birdscreen with 1/2 inch square mesh for exhaust and 3/4 inch for intake.

B. Fabricate of [16 gage galvanized steel] [or] [0.081 inch thick] [12 gage extruded aluminum], welded assembly, with factory [prime coat] [baked enamel] [color anodized] finish.

C. Furnish with [interior] [exterior] [flat flange] [angle flange] [screw holes in jambs] [masonry strap anchors] for installation.

D. Fabricate louver penthouses with mitered corners and reinforce with structural angles.

2.02 ROOF HOODS

A. Fabricate air inlet or exhaust hoods in accordance with SMACNA Low Pressure Duct Construction Standards.

B. Fabricate of galvanized steel, minimum 16 gage base and 20 gage hood, or aluminum, minimum 16 gage base and 18 gage hood; suitably reinforced; with removable hood; birdscreen with 1/2 inch square mesh for exhaust and 3/4 inch for intake, and factory [prime coat] [baked enamel] finish.

C. Mount unit on minimum 12 inch high factory fabricated curb base with insulation between duct and curb.

D. Make hood outlet area minimum of twice throat area.

3.00 EXECUTION

3.01 INSTALLATION

A. Check location of outlets and inlets and make necessary adjustments in position to conform with architectural features, symmetry, and arrangement.

B. Furnish all necessary miscellaneous steel framing for support of intake and relief ventilations.

END OF SECTION

G:\spec revision\M\15941m.new.doc
MASTER MECHANICAL
SECTION 15941 - 2
SPECIFICATION
INTAKE AND RELIEF VENTILATORS


REV. 03/00


