G:\spec revision\M\15973M.NEW.doc

SECTION 15973

PNEUMATIC CONTROL SYSTEMS

NOTE:
THIS IS NOT A MASTER.  DETAILED EDITING IS REQUIRED FOR EACH PROJECT.

1.00 GENERAL

1.01 PRINCIPAL WORK IN THIS SECTION

A. Air compressor and receiver.

B. Compressed air piping.

C. Refrigerated air dryer.

D. Thermostats.

E. Humidistat.

F. Control valves.

G. Automatic dampers.

H. Damper operators.

I. Highest/lowest/averaging signal selector.

J. Multi-purpose positioning relays.

K. Time clocks.

L. Transmitters.

M. Receiver controller.

N. Miscellaneous accessories.

O. Control panel.

P. Alarm system.

1.02 PRODUCTS FURNISHED BUT NOT INSTALLED UNDER THIS SECTION

A. Section 15510 - Hydronic Piping: Installation of control valves, flow switches, temperature sensor sockets, gage taps.

B. Section 15520 - Steam and Condensate Piping: Installation of control valves, flow switches, temperature sensor sockets, gage taps.

C. Section 15910 - Ductwork Accessories: Installation of automatic dampers.

1.03 PRODUCTS INSTALLED BUT NOT FURNISHED UNDER THIS SECTION

A. Section 15658 - Reciprocating Refrigerant Compressors: Connection of cylinder unloaders.

B. Section [_____ - __________]: Connect control components factory supplied as part of equipment controlled, unless specified otherwise.

1.04 SYSTEM DESCRIPTION

A. Provide control systems consisting of thermostats, control valves, dampers and operators, indicating devices, interface equipment and other apparatus and accessories required to operate mechanical systems, and to perform functions specified.

B. Provide pneumatic automatic temperature control systems with electric accessories.

1.05 SUBMITTALS

A. Shop Drawings: Indicate complete operating data, system drawings, wiring diagrams, and written detailed operational description of sequences.  For automatic dampers indicate arrangement, velocities, and static pressure drops for each system.

B. Product Data: Include description and engineering data for each control system component.  Include sizing as requested.

C. Samples: Submit [two] [_____] of [each type of room thermostat and cover.] [thermostat guard.] [each exposed control component.]

D. Design Data: Submit design data indicating [sizing and selection of compressor.] [sizing of air tubing.] [__________.]

E. Submittals of automatic control systems components which are not the product of the control system manufacturer shall bear evidence of his approval.

F. Submit field reports indicating operating conditions after detailed check out of systems at Date of Substantial Completion.

1.06 PROJECT RECORD DOCUMENTS

A. Accurately record actual location of control components, including panels, thermostats, and sensors.

1.07 OPERATION AND MAINTENANCE DATA

A. Include systems descriptions, set points, and controls settings and adjustments.

B. Include inspection period, cleaning methods, recommended cleaning materials, and calibration tolerances.

1.08 QUALIFICATIONS

A. Design system under direct supervision of a Professional Engineer experienced in design of this work.

1.09 MAINTENANCE SERVICE

A. Furnish service and maintenance of automatic controls system for [one] [_____] year from Date of Substantial Completion.

B. Provide [two] [four] [_____] complete inspections, to inspect, calibrate, and adjust controls as required, and submit written reports.

OR

C. Provide complete service of controls systems, including call backs.  Make minimum of [_____] complete normal inspections of approximately [_____] hours duration in addition to normal service calls to inspect, calibrate, and adjust controls, and submit written reports.

1.010 EXTRA MATERIALS

A. Provide [two] [_____] of each type thermostat [,] [and] [__________].

2.00 PRODUCTS

2.01 MANUFACTURERS

A. [______________________________] Product [_____________.]

B. [______________________________] Product [_____________.]

C. [______________________________] Product [_____________.]

2.02 AIR SUPPLY

A. Air Supply and Receiver: [Simplex] [Duplex] belt driven air compressor and tank unit with belt guard, silencers, flexible connections, air filter, automatic and manual drain assemblies, oil and particle filter for minimum 0.5 micron particles, pressure reducing valves, and pressure relief valves.  Size [each] compressor and storage tank to limit compressor starts to maximum [10] [_____] per hour and [50] [30] percent running time.

B. Pressure Control: Zinc or aluminum castings, rated for service with elastomeric diaphragm, adjustable electric contacts, set to start and stop compressor at [50 and 65 psig] [60 and 80 psig] [70 and 90 psig] [100 and 125 psig][.][,] [and second compressor at [50 and 65 psig] [60 and 80 psig] [70 and 90 psig].]

C. Electrical Alternation Set: With motor starters to operate compressors [alternately.] [on time schedule.]

D. Pressure Regulators: Zinc or aluminum castings, rated for service with elastomeric diaphragm, balanced construction to automatically prevent pressure buildup, and producing flat, reduced pressure curve for system capacity demand.

E. Particle Filters: Zinc or aluminum castings, rated for service with threaded connections, quick-disconnect service devices, aluminum bowl or plastic bowl with metal guard equipped with manual draincock, to separate liquid and solid particles.

F. Combination Filter/Regulators: Zinc or aluminum castings, rated for service with elastomeric diaphragm, balanced construction to automatically prevent pressure buildup, and producing flat, reduced pressure curve for system capacity demand; with threaded pipe connections, quick- disconnect service devices, aluminum bowl or plastic bowl with metal guard equipped with manual draincock to separate liquid and solid particles.

G. Airborne Oil Filter: Rated for service with filtration efficiencies of 99.9 percent for particles of 0.025 micron or larger particles of airborne lubricating oil.

H. Pressure Relief Valves: ASME Code Rated and labeled for high pressure side and sized for installed capacity of pressure regulators at low pressure.  Set at maximum 20 percent above low pressure.

2.03 CONTROL AND INSTRUMENTATION TUBING

A. Copper Tubing: ASTM B280, Type K, seamless, hard drawn or annealed.

1. Fittings: ANSI/ASME B16.22, wrought copper.

2. Joints: ANSI/ASTM B32 [or FS QQ-S-571 alloy 58-5] [95-5] [60-4] tin antimony.

B. Copper Tubing: ASTM B280, Type K, seamless, hard drawn or annealed.

1. Fittings: UL approved [to MIL-F-18280] rod or forged brass rated to 200 psig at 100ºF.

2. Joints: Ball Sleeve compression type.

C. Polyethylene Tubing: Black, flame retardant, virgin polyethylene, conforming to modified ASTM D1693 test.

1. Fittings: UL approved [to MIL-F-18280] rod or forged brass rated to 200 psig at 100ºF.

2. Joints: Compression or barbed type.

2.04 REFRIGERATED AIR DRYER

A. General Assembly: Self-contained, commercial quality, refrigerated, compressed air dryer complete with heat exchangers, moisture separator, and internal wiring and piping.  Provide air inlet and outlet connections connected through manual by-pass valve.

B. Heat Exchangers: Air to refrigerant coils.  Provide centrifugal type moisture separator located at discharge of compressed air complete with automatic trap assembly. Provide automatic control system to bypass refrigeration system on low or no load conditions.

C. Refrigeration Unit: Hermetically sealed, operating to maintain dew point of [5] [13]ºF at 20 psig.  House in steel cabinet with access door and panel.

D. Accessories: Air inlet temperature gage, air inlet pressure gage, on/off switch, high temperature light, power on light, refrigerant gage on back, air outlet temperature gage, air outlet pressure gage.

2.05 THERMOSTATS

A. Pneumatic Room Thermostats: Adjustable proportioning type, [single] [dual] setpoint, containing [single bimetallic element for heating or cooling only] [dual bimetallic elements for] [heating and cooling] [day or night], minimum 10ºF set point adjustment[.] [and] adjustable dead band.] Provide locking covers with [set point adjustment,] [setpoint indication,] [concealed setpoint,] [with thermometer.] [without thermometer.]

B. Electric Room Thermostats: [NEMA DC 3] Low voltage type [with setback/setup temperature control] for [cooling only.] [heating only.] [cooling and heating.] [Conform to MIL-S-29175.]

C. Line Voltage Thermostats: Integral manual On/Off/Auto selector switch, maximum dead band of 2ºF concealed temperature adjustment, and locking cover, rated for [motor] load, single or two pole as required.

D. Room Thermostat Accessories:

1. Thermostat Covers: [Brushed aluminum.] [_________.]

2. Insulating Bases: For thermostats located on exterior walls.

3. Thermostat Guards: [Metal] [Locking transparent plastic] [__________] mounted on separate base.

4. Adjusting Key: As required for device.

E. Outdoor Reset Thermostat: Remote bulb or bimetal rod and tube type, for proportioning action with adjustable throttling range; scale range of [-10 to 70ºF] [__________] with adjustable setpoint.

F. Immersion Thermostat: Remote bulb or bimetallic rod and tube type, for proportional action with adjustable setpoint and adjustable throttling range.

G. Airstream Thermostats: Remote bulb or bimetallic rod and tube type, for proportional action with adjustable setpoint in middle of range and adjustable throttling range.  For averaging service provide remote bulb element [7.5 feet.] [20 feet.]

H. Electric Low Limit Duct Thermostat: Snap acting, single pole, single throw, manual reset switch which trips if temperature sensed across any 12 inches of bulb length is equal to or below setpoint, requiring minimum [20] [_____] feet length of bulb.  Provide one thermostat for every 20 sq. ft. of coil surface.

I. Electric High  Limit Duct Thermostat: Snap acting, single pole, single throw, manual reset switch which trips if temperature sensed across any 12 inches of bulb length, is equal to or above setpoint, requiring minimum 20 feet length of bulb.  Provide one thermostat for every 20 sq ft of coil surface.

J. Fire Thermostats: UL approved and listed, factory set in accordance with ANSI/NFPA 90A with normally closed contacts, manual reset.

K. Heating/Cooling Valve Top Thermostats: Proportional acting for proportional flow, molded rubber diaphragm, [remote bulb] liquid filled element, direct and reverse acting at differential pressures to 25 psig, cast housing with position indicator and adjusting knob.

2.06 HUMIDISTAT

A. Room Humidistat: Wall mounted, proportioning type, with adjustable [2] [5] percent relative humidity throttling range, operating range from [30 to 80] [_____] percent at temperatures up to [110] [_____]ºF, cover with [set point indication.] [concealed setpoint.]

B. Duct Humidistat: Insertion type, proportioning type, with adjustable 2 percent relative humidity throttling range, operating range from 20 to 80 percent at temperatures up to 150ºF.

C. High Limit Duct Humidistat: Insertion type, reverse acting, two position type, with differential maximum 2 percent relative humidity.

2.07 CONTROL VALVES

A. Globe Pattern:

1. Up to 2 inches: Bronze body, bronze trim, rising stem, renewable composition disc, screwed ends[,][.] [with backseating capacity repackable under pressure.]

2. Over 2 inches: Iron body, bronze trim, rising stem, plug-type disc, flanged ends, renewable seat and disc.

B. Butterfly Pattern: Iron body, [bronze] [aluminum bronze] [stainless steel] disc, resilient replaceable seat for service to [180ºF] [250ºF] wafer or long ends, extended neck.

C. Operators:

1. Rolling diaphragm, spring loaded, piston type with spring range [2 to 5 psig.] [3 to 10 psig.] [8 to 11 psig.] 

2. Valves shall spring return to normal position as indicated on freeze, fire, or temperature protection.

D. Hydronic Systems:

1. Rate for service pressure of 125 psig at 250ºF.

2. Replaceable plugs and seats of [stainless steel.] [brass.]

3. Size for [3] [_____] psig maximum pressure drop at design flow rate.

4. Two way valves shall have equal percentage characteristics, three way valves linear characteristics.  Size two way valve operators to close valves against pump shut off head.

E. Steam Systems:

1. Rate for service pressure of 125 psig at 250ºF.

2. Replaceable plugs and seats of stainless steel. Pressure drop across any steam valve at maximum flow shall be as shown on the Drawings.

3. Size for 10 psig inlet pressure and 5 psig pressure drop.

4. Valves shall have modified linear characteristics.

2.08 DAMPERS

A. Performance: Test in accordance with AMCA 500.

B. Frames: [Galvanized steel] [Extruded aluminum] [Rolled carbon steel] [Stainless steel], welded or riveted with corner reinforcement.

C. Blades: [Galvanized steel] [Extruded aluminum] [Rolled carbon steel] [Stainless steel], maximum blade size [8] [___] inches wide, 48 inches long, attached to minimum 1/2 inch shafts with set screws.

D. Blade Seals: [Synthetic elastomeric] [Neoprene] [inflatable] mechanically attached, field replaceable.

E. Jamb Seals: Stainless steel.

F. Shaft Bearings: [Oil impregnated sintered bronze or graphite impregnated nylon sleeve, with thrust washers at bearings.] [Lubricant free, stainless steel, single row, unground, flanged, radial, antifriction type with extended inner race.]

G. Linkage Bearings: Oil impregnated sintered bronze or graphite impregnated nylon.

H. Leakage: Less than [one] [1/2] percent based on approach velocity of 2000 ft/min 4 inches wg.

I. Maximum Pressure Differential: 6 inches wg.

J. Temperature Limits: -40 to 200ºF.

2.09 DAMPER OPERATORS

A. General: Provide smooth proportional control with sufficient power for air velocities 20 percent greater than maximum design velocity and to provide tight seal against maximum system pressures.  Provide spring return for two position control and for fail safe operation.

B. Pneumatic Operators: Rolling diaphragm piston type[.] [with adjustable stops.]

C. Pilot Positioners: Starting point adjustable from 2 to 12 psig and operating span adjustable from 5 to 13 psig.

D. Electric Operators: Split phase type with oil immersed gear train.

E. Number: Sufficient to achieve unrestricted movement throughout damper range.  [Provide one damper operator for maximum 36 sq ft damper section.]

F. Inlet Vane Operators: High pressure with pilot positioners and sufficient force to move vanes when fan is started with vanes in closed position.  Return vane operator to closed position on fan shutdown.

2.010 TIME CLOCKS

A. Seven day programming switch timer with synchronous timing motor and seven day dial, continuously charged Ni-cad battery driven power failure 8 hour carry over and multiple switch trippers to control systems for minimum of two and maximum of eight signals per day with two normally open and two normally closed output switches.

B. Solid state programmable time control with [_____] separate programs, 24 hour battery carry over[,][.] [duty cycling] [individual on/off/auto switches for each program] [7 day programming] [365 day calendar with 20 programmable holidays] [choice of fail safe operation for each program] [system fault alarm].

2.011 WATER TEMPERATURE CONTROLLERS

A. Operate on adjustable differential over adjustable temperature range and suitable for operating control valve provided.

2.012 TRANSMITTERS

A. Building Static Pressure Transmitter: One pipe, [direct acting, double bell,] differential type with temperature compensation, scale range 0.01 to 6.0 inch wg positive or negative, and sensitivity of 0.0005 inch wg.  Transmit [electronic] [pneumatic] signal to receiver with matched scale range.

B. Pressure Transmitters: One pipe direct acting [indicating type] for gas, liquid, or steam service, range suitable for system, proportional [electronic] [pneumatic] output.

C. Temperature Transmitters: One pipe, directly proportional output signal to measured variable, linearity within plus or minus 1/2 percent of range for 200 degree F span and plus or minus one percent for 50 degree F span, with 50, 100, or 200 degree F temperature range, compensated bulb, averaging capillary, or rod and tube operating on 20 psig input pressure and 3 to 15 psig output.

D. Humidity Transmitters: One pipe, directly proportioned output signal to measured variable, linearity within plus or minus one percent for 70 percent relative humidity span, capable of withstanding 95 percent relative humidity without loss of calibration.

2.013 RECEIVER CONTROLLERS

A. Single or dual input models [with control point adjustment] direct or reverse acting with mechanical set point adjustment [with locking device], proportional band adjustment, and authority adjustment.  Provide [proportional] [proportional plus integral] control mode.

B. Remote control point adjustment shall be plus or minus [20] [___] percent of sensor span, input signal [3 to 13 psig.] [1 to 20 psig.]

C. Proportional band shall extend from 2-1/2 to 40 percent of primary sensor span, authority from 10 to 200 percent of primary sensor span[.] [and integral time 0.5 to 20 min.]

D. Suitable for supply air pressure of [18 psig] [20 psig] with input signals of [3 to 15 psig] [1 to 20 psig] and output signal 0 to [15 psig.] [20 psig.]

2.014 PNEUMATIC SYSTEMS ACCESSORIES

A. Pressure Gages: Manufacturer's standard [to FS-GG-G-76], black letters on white background, [3-1/2 inch] [2-1/2 inch] [2 inch] diameter, flush or surface mounted, with [front calibration screw,] suitable dial range calibrated to match sensor, in appropriate units.

B. Instrument Pressure Gages: Manufacturer's standard [to FS-GG-G-76], black letters on white background, [2 inch] [1-1/2 inch] diameter, stem mounted with suitable dial range.

C. Diaphragm Control and Instrument Valves: 1/4 and 3/8 inch forged brass body with reinforced teflon diaphragm, stainless steel spring, and color coded phenolic handle.

D. Gage Cocks: Tee or lever handle, bronze, rated for 125 psig.

E. Relays: For summing, reversing, amplifying, highest or lowest pressure selection, with fixed 1:1 [or adjustable] input/output ratio.

F. Switches: With indicating plates, accessible adjustment, calibrated and marked.

2.015 CONTROL PANELS

A. Unitized cabinet type for each system under automatic control with relays and controls mounted in cabinet and temperature indicators, pressure gages, pilot lights, pushbuttons and switches flush on cabinet panel face.

B. ANSI/NEMA 250, general purpose utility enclosures with enamelled finished face panel.

2.016 ALARM SYSTEM

A. Provide alarm panel with individual indication, horn, silenced acknowledge switch, and test switch.

B. At any alarm condition indication light will flash and alarm will sound.  Stop horn by depressing acknowledge switch and indicate alarm conditions by a continuous light until trouble condition has cleared.  Sound alarm again should second alarm occur before first one has cleared.

C. Provide remote panels where indicated with indication horn, activated by any alarm.  Provide alarm silence/acknowledge switch such that alarm can be acknowledged from master and remote panel.

D. Provide panels in locations described to serve duplicate functions of primary panel.  Provide alarm silence/acknowledge switch such that alarm can be acknowledged from any panel.

E. Provide dry contacts at main alarm panel for use by independent alarm monitoring company to indicate [each] alarm condition.

3.00 EXECUTION

3.01 EXAMINATION

A. Verify that systems are ready to receive work.

B. Beginning of installation means installer accepts existing conditions.

3.02 INSTALLATION

A. Install in accordance with manufacturer's instructions.

B. Mount compressor and tank unit on vibration isolation[.] [consisting of springs, with minimum [one inch] [2 inches] static deflection and one inch (25 mm) clearance to floor.] [Refer to Section 15242.] Isolate air supply with wire-braid reinforced rubber hose[.] [or polyethylene tubing.]

C. Supply instrument air from compressor units through filter, pressure reducing valve, pressure relief valve, with pressure gages, and shutoff and bypass valves.

D. Install pressure reducing stations consisting of pressure reducing valve, particle filter, valved bypass, pressure gage on inlet and outlet, and pressure relief valve.

E. Locate refrigerated air dryer in discharge air line from tank.  Mount dryer on wall on rubber in shear mounts. Install pressure regulator downstream of dryer.  Pipe automatic drain to nearest floor drain.

F. Use copper tubing in mechanical rooms, where subject to damage or temperatures in excess of 200ºF), where adjacent to heating pipes passing through common sleeve, and where not readily accessible. In mechanical rooms bundled plastic tubing with suitable junction boxes or single plastic tubing with tray or raceway may be used.

G. Conceal tubing.  Run exposed only in mechanical rooms, storage rooms and like, in neat manner and properly supported.  [Refer to Section 15140.]

H. Mechanically attach tubing to supporting surfaces.  Sleeve through concrete surfaces in minimum one inch sleeves, extended 6 inches above floors and one inch below bottom surface of slabs.

I. Purge tubing with dry, oil-free compressed air before connecting control instruments.

J. Provide instrument air tubing with check and hand valves to expansion tanks with Schraeder fittings and hose.

K. Install [pressure gages] [test plugs] on branch lines at each receiver controller and signal lines at each transmitter excepting individual room controllers.

L. Check and verify location of thermostats[,] [humidistat,] and other exposed control sensors with plans and room details before installation.  Locate room thermostats [60 inches] [48 inches] [42 inches] above floor.  Align with lighting switches[,][.] [and humidistat.]

M. Mount freeze protection thermostats using flanges and element holders.

N. Mount outdoor reset thermostats and outdoor sensors indoors, with sensing elements outdoors[.] [with sun shield.]

O. Provide separable sockets for liquids and flanges for air bulb elements.  Refer to Section 15980.

P. Provide thermostats in aspirating boxes in front entrances[,] [handball courts,] [gymnasiums,] [high security areas] [and] [__________.] [and where indicated.]

Q. Provide guards on thermostats in entrance hallways [and other public areas.] [and where indicated.]

R. Provide valves with position indicators and with pilot positioners where sequenced with other controls.

S. Provide separate steam valve for each bank of coils. Provide two valves in parallel where steam load exceeds 1500 lb/hr.  Capacities for two valves in parallel shall have 1/3 - 2/3 load capacities sequenced with smaller valve opening first.

T. Provide mixing dampers of [opposed] [or] [parallel] blade construction arranged to mix streams.  Provide pilot positioners on mixed air damper motors.  [Provide separate minimum outside air damper section adjacent to return air dampers with separate damper motor.]

U. Provide pilot positioners on damper operators sequenced with other controls.

V. Test multizone dampers for temperature pickup due to leakage when hot deck is closed and cold deck is open. Adjust for maximum temperature rise of 2ºF when the temperature difference between the hot and cold decks is 20ºF.

W. Mount control panels adjacent to associated equipment on vibration free walls or free standing angle iron supports. One cabinet may accommodate more than one system in same equipment room.  Provide engraved plastic nameplates for instruments and controls inside cabinet and engraved lamicoid nameplates on cabinet face.

X. Install "hand/off/auto" selector switches to over-ride automatic interlock controls when switch is in "hand" position.

Y. Provide conduit and electrical control wiring.  Power wiring by Division 16.

Z. After completion of installation, test and adjust control equipment.  Submit data showing set points and final adjustments of controls.

AA. Test pneumatic systems to system pressure maximum of 30 psig. Check calibration of instruments.  Recalibrate or replace.

3.03 DEMONSTRATION

A. Demonstrate complete operation of systems, including sequence of operation after Date of Substantial Completion.

END OF SECTION

G:\PUBLIC\MASTER\WRD97SPC\M\15973M.DOC
MASTER MECHANICAL
SECTION 15973 - 13
SPECIFICATION
PNEUMATIC CONTROL SYSTEMS


REV. 12/99


